## Slide 1: Process Controllers
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation

## Slide 2: Controllers
Controllers:
  An electronic (Digital) or pneumatic computing device that compares a Setpoint Value to a Process Value and adjusts it’s output to cause the loop error to be driven towards zero.
    The most common controller is the PID controller
      PID = Proportional, Integral, Derivative

## Slide 3: MOST Common PID Variations
  PO; Proportional Only (Single Mode)
    Gain Only
  PI; Proportional + Integral (Two Mode)
    Proportional + Reset
    Gain + Integral
  PID; Proportional + Integral + Derivative (Three Mode)
    Proportional + Reset + Rate
    Gain + Integral + Derivative

## Slide 4: Controller Terms
Pneumatic
Proportional Band (PB)
Reset
Rate
Electronic/Digital
Gain (Kc)
Integral
Derivative

## Slide 5: Proportional Band / Gain
  The most basic continuous control mode is proportional control where the controller output is algebraically proportional to the calculated error (SP-PV) input signal to the controller.
  %ΔMV (Δ%output) = Kce
    The gain of the controller is the term Kc.
      Note: All controllers do the calculations in Percent
  It indicates the change in the manipulated variable per unit change in the error signal.
    The percentage of controller input span required to change the output 100%

## Slide 6: Proportional vs. Gain
  PB and Gain both describe the controller’s reaction to a step change
  They are the reciprocal of each other.
  PB (%) = 100/Kc

## Slide 7
Gain = 1
PB = 100%
Gain = 2
PB = 50%
Gain = 10
PB = 10%
Gain = .5
PB = 200%

## Slide 8
Proportional Band % = 100/Proportional Gain | 
Proportional Band | Gain
1% | 100.0
10% | 10.0
50% | 2.0
100% | 1.0
500% | 0.2
1000% | 0.1

## Slide 9: Proportional & Gain
  Reacts only to a change (single step)
  Results in proportional “offset”
  Generally a stabilizing action

## Slide 10
Setpoint
Process Variable
Proportional
Offset
Controller Output

## Slide 11: Reset/Integral
  Reduces error
  Integrates the magnitude of continuing error (P offset) as a function of time and repeats the PB/Gain action
  Tends to be de-stabilizing
  Repeat is measured in Unit of Time/Repeat or Repeats/Unit of Time
    Minutes/Repeats
    Repeats/Minute

## Slide 12
Setpoint
Controller Output
Integral/Reset
Action
Process Variable

## Slide 13
Seconds per repeat (DeltaV) | Repeats per second | Minutes per repeat | Repeats per minute
1 | 1 | 0.0167 | 60.0
5 | 0.20 | 0.0833 | 12.0
10 | 0.1. | 0.167 | 6.0
60 | 0.167 | 1.0 | 1.0
120 | 0.0083 | 2.0 | 0.5
240 | 0.00417 | 4.0 | 0.25
480 | 0.00208 | 8.0 | 0.125
1200 | 0.00083 | 20 | 0.050

## Slide 14: Derivative
  Reacts to the rate & direction of changes
  Additive to the Gain action
  By adding derivative mode to the controller, lead is added in the controller to compensate for lag around the loop.
  Quasi FF
  Very De-stabilizing
  Used only with very Slow and Quiet Processes (Temp)

## Slide 15: Controller Outputs
Controller
Output