## Slide 1: Process II
Process Types & Dynamics
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Process Loop Types
Self Regulating:
  The ability or tendency of the process to maintain equilibrium
  Generally will only maintain equilibrium with in a vary defined set of limits and range or type of disturbance(s).
  In real life very few processes are self regulating

## Slide 3: Process Loop Types
Non-self Regulating or Integrating
  Any Process which will not reach equilibrium on its own.
    The process will continue changing until is meets a physical constraint
  Basically everything we deal with as process operators.

## Slide 4: Process Loop Characteristics
There are several terms to describe various process loop characteristics
By ACTION:
  Direct:
    The process variable will react to a change in setpoint in the same direction as the change.
      Increase the setpoint the process variable increases.
    The process variable will react in an intuitive manner to a disturbance.

## Slide 5: Process Loop Characteristics
  Inverse:
    The process variable will generally react to a change in setpoint in the opposite direction as the change.
      Increase the setpoint the process variable decreases.
    The process variable will react in a counterintuitive manner to a disturbance.
      Boiler drum level

## Slide 6: Process Dynamics
PROCESS DYNAMICS:
  How the control loop responses to a change in input or load relative to TIME/SPEED and SHAPE of the response curve/trend.
  Terms used to describe the loop dynamics
    Gain
    1st Order, 2nd Order……
    Dead Time
    Resistance
    Capacitance
    Time Constant

## Slide 7: Process Dynamics
Process Loop Dynamics Testing
  Loop dynamic testing requires doing a loop “bump” test
  Loop is always in manual
  Requires some form of recording/trending apparatus
  Process is given a series of SMALL bumps (e.g., 1%, 2.5%, 5%, etc.)
    The output of the controller is adjusted (bumped)
  Results are recorded and analyzed.

## Slide 8: Process Dynamics
Process Dead Time
  The time period after a change has occurred, during which the measurements are not affected.
  Transportation time is an example.
  Dead time is one of the worst enemies of good control.

## Slide 9: Process Dynamics
Process Gain
  The steady state change in the PV resulting from a measured change in the MV.
  Tested with the loop controller in manual.
  Gain (kc)= Δoutput/%Δinput
  To calculate:
    Step the MV (controller output) a specific amount (e.g. 1%, 2.5%, 5%, 10%, etc.)
    Observe and record the PV response
    Calculate the percent (%) change in PV
    Divide the percent (%) change in the PV by the step percent (%) change in the MV.

## Slide 10: Process Dynamics
Time Constant(s)
  Measure of time required for something to react to a change.
  A process typically has multiple time constants.
  Time constants are generally additive and contribute to the speed of response of the process loop
Process Time Constant
  The time required by the process variable to reach 63% of its total response to a step change in the MV.
  It is a standardized way of measuring and describing all of the loop’s the individual time constants combined except the controller

## Slide 11: Process Dynamics
Resistance
  Pressure drops through piping most common.
Capacitance
  Any location where the process is able to store mass or energy.
  Tanks & Headers are examples of capacitance