## Slide 1
ACADs (08-006) Covered
Keywords
Prints, drawings, piping and instrumentation, one-line drawing, elementary drawing, logic prints, drawing layout, document numbering system, revision record, symbols, logic.
Description
Supporting Material
Electrical Prints and Drawings
2.2.16 | 5.1.1.2.1.7 | 5.1.2.18 | 5.4.1.3 |  |  |  | 

## Slide 2: Electrical Prints and Drawings
Reading and Interpreting Prints and Drawings

## Slide 3
Title | Electrical Prints and Drawings |  | 
Number | AT-1160-LP-Elect P&D |  | 
Program | NET NLO |  | 
Author | Alex Ramos | 5/11/11 | AWR
IT Review |  |  | 
Approved |  |  | 
Instructor Guidelines
Lesson Format – PowerPoint Presentation
Materials – Computer, Projector
Evaluation – None
Remarks – None
References – Various Plant Drawings

## Slide 4: Record of Revision
Rev | Date | Reason for Revision | Author’s Initials | Supv’s Initials
0 | 5/04/11 | Initial Development | AWR | 

## Slide 5: Objectives
DESCRIBE the information found on the following types of prints and drawings:
  P&IDs
  Electrical One-Line Drawings
  Electrical Elementary Drawings
  Logic Prints
RECOGNIZE commonly used print and drawing symbology.
    DESCRIBE how to obtain the latest approved version of plant prints and drawings.

## Slide 6: Types of Prints/Drawings
Piping and Instrumentation Drawing (P&ID)
  Present functional information about a system or component (Not drawn to scale)
Electrical One-Line Diagram
  Present functional information about electrical design of a system or component (Not drawn to scale)

## Slide 7: Types of Prints/Drawings
Electrical Elementary Diagram
  Present information such as individual relays, relay contacts, fuses, motors, lights, instrument sensors, etc.
Logic Prints (Logics)
  Present “simplified” functional representation of a control (electrical) circuit

## Slide 8: Types of Prints/Drawings
Others
  Data Sheets
  Isometrics
  Flow Diagrams
  Architectural Drawings
  Loop Diagrams

## Slide 9: Obtaining Drawings/Prints
Existing Controlled Copies
  Document Control
  Controlled Records
    Operations
    “Documentum”
Printed from LAN (Documentum) – will be most current version of drawing

## Slide 10: Obtaining Drawings/Prints
Previously printed drawing – must verify correct revision number
  Verify revision number on Documentum after 7 days
  Must check revision number correct every day after 7 days

## Slide 11: Engineering Drawing Layout
Engineering drawing can be divided into five major areas or parts
  Title block
  Grid system
  Revision block
  Notes and legends
  Engineering drawing (graphic portion)

## Slide 12: Title Block

## Slide 13: Document Numbering System
Consists of 6, 7, or 8 elements, depending on type of drawing
  Mechanical Drawings - 6 elements
  Certain Control Systems Drawings – 7 elements
  Architectural Drawings – 7 elements
  Electrical Drawings - 8 elements

## Slide 14: Document Numbering System
First 4 elements common to all types of drawings
1st Element – Unit
  "1 or 2" designates unit
  "A" designates - Shared by units 1 and 2 - Systems and structures specific to units 1 and 2 within the power block, or its proximity
  "C" designates - Common to site -Items that require only one system, structure, or common location for both units 1 and 2 (entire site)

## Slide 15: Document Numbering System
2nd Element - Project
  Always "X" for drawings
  Designates Bechtel job number for construction of Plant Vogtle

## Slide 16: Document Numbering System
3rd Element – Discipline
  "1" - Architectural
  "2" - Civil-structural
  "3" - Electrical
  "4" - Mechanical
  "5" – Control
4th Element - Bechtel drawing
  Always "D"

## Slide 17: Document Numbering System
  Mechanical Drawings – Discipline 4
  5th Element - Subject
    "A" not used
    "B" - P&ID
    "C" - heat balance
    "D" - general arrangements and mechanical plot plan
    "E" - equipment locations
    "F" - drawing indexes
    "G" - critical piping
    "R" - selected engineering documents
    "T" - temporary systems

## Slide 18: Document Numbering System
  Mechanical Drawings – Discipline 4
  6th Element – Drawing sequence number
    3 digit number (i.e. 122)
    May be followed by sheet number (i.e. 122-1, 122-2, etc.)

## Slide 19: Document Numbering System
  Example:
  AX4DB001
    "A“ - Common to both units
    "X“ - Drawing
    "4“ - Mechanical
    "D“ - Plant Vogtle (Bechtel Drawing)
    "B“ - P&ID
    "001“ - Sequence

## Slide 20: Document Numbering System
  Electrical (Wiring) Drawings - Discipline 3
  5th Element - Type of drawing
    "A" - one-line diagram, general notes, symbols, numbering system, abbreviations, and main one-line
    "B" - elementary
    "C" - wiring

## Slide 21: Document Numbering System
  Electrical (Wiring) Drawings - Discipline 3
  6th Element - System
    "A" - electrical systems/all systems
    "B" - turbine/generator
    "C" - balance of plant
    "D" - reactor (Nuclear Steam Supply System [NSSS])
    "E" - control boards, miscellaneous panels and systems
    "F“ - not used
    "G" - HVAC
    "H" - miscellaneous auxiliary systems

## Slide 22: Document Numbering System
  Electrical Drawings - Discipline 3
  7th Element - Specific subject/system categories as listed under the general notes and symbol drawing (1X3D-AA-A00A)
  8th Element - sequence number
    3-character alphanumeric consisting of two numerals and a letter, i.e., 00A, 00B, etc.
    Indicates sequence within subject/system category

## Slide 23: Document Numbering System
  Example:
  1X3D-BD-C034
    "1“ – Unit 1
    "X“ - Drawing
    "3“ - Electrical Discipline
    "D“ - Plant Vogtle (Bechtel Drawing)
    "B“ - Elementary diagram
    "D“ - Reactor (Nuclear Steam Supply System {NSSS})
    "C" - CVCS - (from 1X3D-AA-A00A legend for drawing series)
    "034“ - Sequence

## Slide 24: Document Numbering System
  Control Systems Drawings – Discipline 5
  5th Element - Subject and/or type
    “A/B/C/D”- data sheets for pressure/temperature/level/flow instruments
    "N" - logic diagrams
    "R/V" - loop diagrams for NSSS/BOP
    "S/W/X" - locations
    "T" - setpoints

## Slide 25: Document Numbering System
  Control Systems Drawings – Discipline 5
  6th Element
    For logics, setpoints, loops, and data sheets this is a three-digit sequence number
    For locations this is the area
  7th Element - two-digit sequence number for control systems location drawings

## Slide 26: Document Numbering System
  Example:
  1X5DN001
    "1“ - Unit 1
    "X“ - Drawing
    "5“ - Control system
    "D“ - Plant Vogtle (Bechtel Drawing)
    "N“ - Logic
    "001“ - Sequence

## Slide 27: Revision Record

## Slide 28: Revision Record
Gives information on current version/revision of drawing
  Reason for revision
  Record of Review and Approval

## Slide 29: Revision Record
ABN – As Built Notice
  Discovered condition (configuration) in field did/does not match latest revision of drawing
DCN (DCP) – Design Change Notice (Package)
  Changes have been made to system configuration
Changes may be enclosed in “cloud” on drawing
  Will have triangle with Rev # enclosed nearby

## Slide 30: Component Symbology

## Slide 31: Component Symbology
Standard engineering symbology used on prints and drawings
  Electrical
  Mechanical
  Instrumentation
First few prints in a series generally give a legend or key for interpreting symbology

## Slide 32: Instrumentation
Letter designations indicate type of instrument
  LIC – Level indicating controller
  TR – Temperature recorder
  FT – “blind” flow transmitter (no indication)
  PIT – Pressure indicating transmitter

## Slide 33: Instrumentation
Instrument Mounting Symbology
Instrument Type / Number in circle
Loop Number also in nearby circle

## Slide 34: Instrumentation
Instrument Board Designations
  Located next to instrument symbol
  Give location of instrument (reading)
  QMCB – Control Room Main Control Board
  PSDA (PSDB) – Plant Shutdown Panel A (B)
  *See Note 16 on 1X4DB102*

## Slide 35: Instrumentation
Computers – elliptical circle enclosing letter designations
  IPC – integrated plant computer
    Blank
    E
    PE
  IPC and PSMS (PSMS designated by “S”)
    PES
    ES

## Slide 36: Instrumentation

## Slide 37: Controls and Indications
HS – Hand Switch
ZS - Position switch
ZL – Position Indication (Light)

## Slide 38: Controls and Indications

## Slide 39: Other Information
Piping Sizes
System Boundaries
  Can distinguish safety-related vs. non-safety-related system based on numbering
    1, 2, 3, 7 ⇒ safety related
System Interfaces
  Information enclosed in arrows gives follow-on (from) system (print) information i.e., (123-1 (G1) )

## Slide 40: Other Information

## Slide 41: Other Information
Alarms
  Diamond-shaped with “A” in center
  Type of alarm designated to left of symbol
    H, H-H, L, etc.
  Panel where alarm received also designated – if no designation ⇒ control room alarm
Interlocks
  Diamond-shaped with “I” in center
  Coincidence next to diamond

## Slide 42: Other Information
Dashed line indicates reactor containment boundary
  IRC
  ORC
“I” inside circle indicates safety-related (injection) component
Containment penetration numbers – number enclosed in diamond
Safety Train Designations (“A” or “B”)

## Slide 43: Other Information
Commonly Used Abbreviations:
  CI – Containment Isolation
  SI – Safety Injection
  CVI – Containment Ventilation Isolation
  CRI – Control Room Isolation
  SLI – Steam Line Isolation
  TT – Turbine Trip
  FI – Feed water Isolation
  CS – Containment Spray actuation
  FHBI – Fuel Handling Building Isolation

## Slide 44: Other Information

## Slide 45: Other Information
Rad Levels
  Indicated by “R” and a Roman Numeral
    R I - <0.25 MR/HR
    R II – 0.25 – 2.5 MR/HR
    R III – 2.5 – 15 MR/HR
    R IV – 15 – 100 MR/HR
    R V – > 100 MR/HR

## Slide 46: Other Information

## Slide 47: Notes Section
Notes referenced with “Note X” near pertinent component
Always read the notes

## Slide 48: Notes Section

## Slide 49: Reading Electrical Prints

## Slide 50: Reading Electrical Prints

## Slide 51: Reading Electrical Prints

## Slide 52: Logics
Provide information on control schemes for equipment using standard Boolean logic
Digital Output signals developed based on digital input signals
  0 or 1
  Off or On
  Low or High

## Slide 53: LOGICS
Key symbols:
  Square box = “and” box
    ALL inputs must be present to box in order to get an output
      If “X” in box, opposite logic (all inputs required for no output)
  Round box = “or” box
    any input(s) result in an output
Various “memory” boxes, time-delay boxes, etc.

## Slide 54: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 1 of 19

## Slide 55: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 1 of 19

## Slide 56: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 1 of 19

## Slide 57: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 1 of 19

## Slide 58: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 2 of 19

## Slide 59: Logics
Notes: From Westinghouse Functional Drawings, PDF Page 6 of 19

## Slide 60: Logics

## Slide 61
Notes: From Westinghouse Functional Drawings, PDF Page 15 of 19

## Slide 62: Logics