## Slide 1
ACADs (08-006) Covered
Keywords
Switchyard, transformer.
Description
Supporting Material
Electrical Distribution
2.1.14.2 | 5.1.1.2.1.7 |  |  |  |  |  | 

## Slide 2: ELECTRICAL DISTRIBUTION

## Slide 3
Title
Electrical Distribution
Author
IT Review
Approved Date
References
Number
Revision
0.0
Program
NLO
Alex Ramos
Date 4/29/11
Date
Lesson Format
PowerPoint Presentation
Materials
Computer Projector and Simulator software
Evaluation
Written exam in conjunction with other lesson plans, presentations,
and handouts.
Remarks
None
P&ID book
Instructor Guidelines
AT-1160-LP-Elect Dist

## Slide 4
Rev No | Date | Reason for Revision | Author’s Initials | Supv’s Initials
0.0 |  | Initial Development for NET Program | AWR | 

## Slide 5: Objectives
Show the layout of a typical Distribution Switchyard to include all power sources and transformers.
Show the different voltage ranges associated with the distribution system
Describe the switchyard configuration when:
a. the main generator is on line
b. the main generator is shutdown
Given a specific electrical distribution label, correctly identify the component, the unit, train, voltage level, and safety type.
For each of the following transformers, be able to describe the purpose and winding voltages:
a. Main Power Transformers (main step-up)
b. Unit Auxiliary Transformers (UAT’s)
c. Reserve Auxiliary Transformers (RAT’s)
d. Standby Auxiliary Transformers (SAT)

## Slide 6: In-Plant Distribution
Switchyard
13.8kV
4.16kV
480V
125VDC
120VAC
Notes: The electrical lesson plan starts at the switchyard and works in to the 120VAC as the flow path above shows.

## Slide 7
4.16KV BUS
1NA05
13.8KV BUS
1NAA
WILSON
(UNDERGROUND)
SAT
13.8 KV SWGR
ANAA
4.16 KV SWGR
ANA04
13.8 KV VOGTLE
OFFSITE POWER
SOURCE NO. 3
DIESEL
GENERATOR
1A
4.16KV BUS
1AA02
13.8KV BUS
1NAB
4.16KV BUS
1NA01
161910
161810
161710
230 KV BUS 2
230 KV BUS 1
A4211
A4213
RAT 1NXRA
161715
161717
161960
161860
161760
161967
UAT 1NXAB
UAT 1NXAA
GENERATOR
UNIT 1
4.16KV BUS
1NA04
A4221
A4223
KI
RAT 1NXRB
161815
161817
161927
161920
161820
161720
DIESEL
GENERATOR
1B
4.16KV BUS
1BA03
KI
MAIN STEP-UP
XFMR 1NXM1
NO
NO
NO
NO
NO
NC
NC
NC
NC
NC
NO
NO
NO
NC
161716
NO
NC
NO
NC
ON - SITE AC
FIGURE 16a-3
LO-TP-01001-004
LO-TP-01101-004
LO-TP-01102-002
NL-TP-01201-005
NC-HO-01501-001
LO-DR-01004-01

## Slide 8
2IM1A
2NXR
RAT A
1NXR
RAT B
2NXM1C
2NXM1B
2NXM1A
1IM1A
1NXA
UAT B
ANXRA
TURBINE BUILDING
1NXM1C
1NXM1B
1NXM1A
RSV AUX XFMR
2NXR
RAT B
230kV LINE
500kV LINE
2NXA
UAT A
1NXR
RAT A
1NXA
UAT A
1NBD
2IM1B
2NXA
UAT B
2NXM1S
1NXM1S
1IM1B
230 KV BUS NO. 1
230 KV BUS NO. 2
$
$
Notes: This is typical for 100% power. The blue lines show the power coming out of the main generators. The red lines show the offsite source and the UAT incoming lines. If you look on the RAT’s, you will notice there are no power coming off the RAT through the 13.8kV side. This is because at greater that 30% power, the RAT’s do not provide power to the 13.8kV system. The alternate incoming breakers are open allowing only the potential to be applied up to the breaker.

## Slide 9
4.16kV
13.8kV
4.16kV
13.8kV
4.16kV
Unit 1 -230kV
Unit 2 -500kV
Input
Output
25kV
Gen Output
25kV
Gen Output
230kV
OffSite
13.8kV
Wilson
Unit Auxiliarys
Reserve Auxiliarys
Standby Auxiliary
Main Step-Ups
TRANSFORMERS
Notes: Here the instructor can briefly describe how the many different transformers here at Vogtle all perform the same function of converting voltages for the different equipment needs. You could explain how the main step-ups and the UATs take their input from the Generator output, the RATs from the 230kV buses and the SAT from Plant Wilson.
Each transformer’s input will appear on a mouse click and the output will automatically come out the other side.

## Slide 10: Transformers
UAT
RAT
Main Step-Ups
SAT

## Slide 11: Main Generator
Source of power to grid
3 phase, 25,000 volts
GE, 4 poles, 60 hertz
Hydrogen cooled
31,177 amps
90% power factor

## Slide 13: Main Transformer
Consists of three single phase transformers
  4th transformer provides standby
  Can be connected to system if needed
Step up transformer increases voltage for distribution
  230,000 volts on unit 1
  500,000 volts on unit 2
Primary side of transformer connected to generator
Secondary side of transformer connected to grid

## Slide 14
Main Step Up Transformers
Notes: The UAT’s and Main Step Up Transformers Oil Pumps are stopped within 3 hours of Transformer de-energization to prevent a static charge buildup from occurring.

## Slide 15: Unit Auxiliary Transformers
Two per unit
Step down transformers decrease voltage for use in plant
Primary side of transformer connected to generator
Two separate secondary windings
  13.8 KV winding connected to 13.8 KV buses
  4160 volt winding connected to 4160 volt buses
Provides power for balance of plant (BOP) loads during normal operations
  Non safety related loads

## Slide 16: Unit Auxiliary Transformers (UAT’s)

## Slide 17: Reserve Auxiliary Transformers
Two per unit
  One spare RAT can be connected within 72 hours
Step down transformers
Primary side of transformer connected to grid
  230 KV for both units 1 & 2
Two separate secondary windings
  13.8 KV winding connected to 13.8 KV buses
  4160 volt winding connected to 4160 volt buses
Provides power for safety related loads in plant
  Can also provide power for non-safety related loads when generator is off line

## Slide 18: Reserve Auxiliary Transformers (RAT’s)
Notes: Due to the 1B RAT having gas problems from a inadvertent small ground in the transformer, a gas monitor system has been installed on this transformer. It is powered from a breaker inside the RAT power cabinet on the side of the transformer. The alarms for the gas monitor are tied in with the RAT oil alarms in a local panel.

## Slide 19: Standby Auxiliary Transformer (SAT)

## Slide 20: Electrical Equipment Labeling
Example 1 A A 02
Unit
Train
Voltage
Sequence
Unit - 1, 2, A common to U1&U2,
or C common to entire Plant
Train- A,B,C,D, or N for Non Safety Related
Voltage- A > 600, B 200 to 600, D- DC

## Slide 21
161526
MAIN STEP UP
TRANSFORMER
2NXM1
GENERATOR
UNIT 2
UNIT AUX.
XFMR 2NXAA
UNIT AUX.
XFMR 2NXAB
RESERVE AUX.
XFMR 2NXRA
RESERVE AUX.
XFMR 2NXRB
2IM1A
161725
2IM1B
161825
A4231
A4233
A4241
A4243
KI
KI
OFFSITE POWER
SOURCE NO. 2
OFFSITE POWER
SOURCE NO. 1
Condensate Pump 1
Condensate Pump 2
Condensate Pump 3
To Modified Ring Bus
To 4.16 kV
Non-ESF
To 4.16 kV
Non-ESF
RCP 3
NO
NC
NC
NO
RCP 1
Circ WTR 2
2NAA
2NAB
RCP 2
RCP 4
Circ WTR 1
1-E BRKRS
1-E BRKRS
To 4.16 kV
ESF
To 4.16 kV
ESF
Notes: This drawing shows the interconnection of the UAT’s and RAT’s with the 13.8kV distribution system. Note to the students how the Non-1E buses have the closest breaker to the RCP’s classified as 1-E. Also, the 13.8kV buses receive power from the RAT’s until power (turbine power 12004-C) gets to 30%, then the buses are transferred to the UAT’s.
The next few slides will deal with the RX trips associated with the 13.8kV buses. A drop in frequency would decrease RCP rotor-power output and the developed torque necessary to supply rated flow. A drop in line voltage would result in excessive reactor coolant pump motor currents which could damage the motor. Time delays on the UV and UF relays will prevent spurious signals from tripping the reactor.

## Slide 22
Main
Gen
FAST BUS TRANSFER
UNIT AUX.
XFMR 2NXAA
To 4.16 kV
Non-ESF
To 4.16 kV
Non-ESF
Generator
Trip Triggers
Fast Bus
(.1 Sec)
Transfer
RES. AUX.
XFMR
Notes: When the slide first comes up you can see the power (red flashing lines) flowing from the generator output through the UAT to the 13.8kV Bus. Main generator lockout relay’s will initiate the transfer on a generator trip signal. If the phase relationship between the voltages is not within the preset tolerance, the fast bus transfer will not occur. However, the 13.8kV buses are also equipped with a residual voltage transfer that acts as a backup to the fast bus transfer. The residual voltage transfer is also actuated by a main generator lockout relay. If a fast bus transfer does not occur following a generator trip, when the bus voltage decays to about 30% of normal, (as sensed by 2 UV relays per bus) the residual voltage transfer will close the bus feeder from the RAT. This occurs only if the feeder from the UAT has opened. There is no requirement for the voltages to be in phase in this case because by the time RAT feeder breaker re-energizes the bus, the existing bus voltage has decayed to essentially zero. The residual voltage transfer takes about 0.9 seconds to occur.

## Slide 23
FAST BUS TRANSFER FOR THE 13.8KV
BUSES 1NAA, 1NAB
161817
161715
161717
NO
NC
GENERATOR
UNIT 1
13.8KV BUS
UAT
1NXAA
MAIN STEP-UP
XFMR 1NXM1
UAT
1NXAB
RAT
1NXRA
13.8KV BUS
RAT
1NXRB
1NA01
1NA05
1NA04
1AA02
1NA05
1NA01
1BA03
1NA04
- INITIATED BY A MAIN GENERATOR TRIP
1NAA
1NAB
NO
NC
161815
OFFSITE POWER SOURCE NO.1
NO. 2

## Slide 24
In-Plant Distribution
Switchyard
13.8kV
4.16kV
480V
125VDC
120VAC

## Slide 25
4.16KV BUS
1NA05
13.8KV BUS
1NAA
WILSON
(UNDERGROUND)
SAT
13.8 KV SWGR
ANAA
4.16 KV SWGR
ANA04
13.8 KV VOGTLE
OFFSITE POWER
SOURCE NO. 3
DIESEL
GENERATOR
1A
4.16KV BUS
1AA02
13.8KV BUS
1NAB
4.16KV BUS
1NA01
161910
161810
161710
230 KV BUS 2
230 KV BUS 1
A4211
A4213
RAT 1NXRA
161715
161717
161960
161860
161760
161967
UAT 1NXAB
UAT 1NXAA
GENERATOR
UNIT 1
4.16KV BUS
1NA04
A4221
A4223
KI
RAT 1NXRB
161815
161817
161927
161920
161820
161720
DIESEL
GENERATOR
1B
4.16KV BUS
1BA03
KI
MAIN STEP-UP
XFMR 1NXM1
NO
NO
NO
NO
NO
NC
NC
NC
NC
NC
NO
NO
NO
NC
161716
NO
NC
NO
NC
ON - SITE AC
FIGURE 16a-3
LO-TP-01001-004
LO-TP-01101-004
LO-TP-01102-002
NL-TP-01201-005
NC-HO-01501-001
LO-DR-01004-01

## Slide 26
161526
MAIN STEP UP
TRANSFORMER
2NXM1
GENERATOR
UNIT 2
UNIT AUX.
XFMR 2NXAA
UNIT AUX.
XFMR 2NXAB
RESERVE AUX.
XFMR 2NXRA
RESERVE AUX.
XFMR 2NXRB
2IM1A
161725
2IM1B
161825
A4231
A4233
A4241
A4243
KI
KI
OFFSITE POWER
SOURCE NO. 2
OFFSITE POWER
SOURCE NO. 1
2NAB
DIESEL
GENERATOR
4.16KV BUS 2AA02
4.16KV BUS 2NA05
4.16KV BUS 2NA01
4.16KV BUS 2NA04
4.16KV BUS 2BA03
NC
NC
NO
NO
NO
NC
NO
NC
NO
NO
NC
NO
DIESEL
GENERATOR
To 13.8 kV
Non-ESF
To 13.8 kV
Non-ESF
To 13.8 kV
Non-ESF
To 13.8 kV
Non-ESF
To Modified Ring Bus
4.16kV 1E Buses
AA02
BA03
4.16kV NON-1E Buses
NA05
NA01
NA04
Residual Bus Transfer
Notes: The NON-1E buses are normally supplied from the UAT’s. They are equipped with a RESIDUAL voltage transfer scheme similar to the 13.8kV buses. When the bus voltage drops to approx. 30%, as sensed by UV relays, the bus feeder from the RAT will close and the UAT feeder will open. NO residual bus transfer scheme is preset for the 4160 ESF buses. The Safety Features Sequencer detects undervoltage conditions on the bus, opens the incoming feeder breaker, starts the diesel, strips loads off the bus, reenergizes the bus from the diesel and places the ESF loads on the bus.
More details about the Sequencer operation and Diesel operation are covered under their associated clusters.

## Slide 27
Switchyard
13.8kV
4.16kV
480V
125VDC
120VAC
In-Plant Distribution

## Slide 28
BULL DOG
ABB
ABD
ABF
ABA
ABC
ABE
FAC
E
BULL DOG FACE
1AB15
1AB05
1AB04
Notes: Use the BULL DOG FACE nuemonic to help remember associated swbds 480 VAC MCC

## Slide 31
Switchyard
13.8kV
4.16kV
480V
125VDC
120VAC
In-Plant Distribution

## Slide 32
Battery Charger
1ND3BCA
Battery Charger
1ND3BCB
Battery Charger
1ND3ACB
Battery Charger
1ND3BCA
Battery Charger
1ND2CA
Battery Charger
1ND1CA
Battery Charger
1ND2CB
Battery Charger
1ND1CB
Control Building
Turbine Building
Turbine Building
1ND3BB
1ND3AB
1ND2B
1ND1B
1ND11
1ND21
1ND33
1ND31
1ND32
To Inverter
1ND3I3
To Inverter
1ND3I1
To Inverter
1ND3I2
To Inverter
1ND3I4
Non-1E 125V DC
1ND3B
1ND3A
1ND2
1ND1
2 Hr
Rating
Notes: The battery charger AC input voltage shall be 480V ± 10 % (432-528V). Normal operation should be one Battery Charger in service with the other charger aligned for standby. Operating experience showed that with no battery on the bus the chargers will both try to carry the loads and will start developing oscillations. If the electrical bus must be energized by the battery chargers alone (without battery breaker closed in), only one charger should be energized to supply the bus.

## Slide 33
1DD1CB
1DD1
1BD1
1DY1B
RHR ISOLATION
VALVE
1BY1B
1BY2B
1DD11
1BD11
1BD12
1BD1M
1DD1B
1BD1B
1DD1I4
1BD1I2
1DD1I6
1BD1I12
1BD1CA
1BD1CB
1BBC
1BBA
125 VDC / 120 VAC CLASS 1E DISTRIBUTION
1BBB
1BBB
1CD1
1CY1A
1CD1M
1CD11
1CD1B
1ABA
125 VDC
125 VDC
125 VDC
120 VAC
1AD1
1AY1A
1AY2A
1AD11
1AD12
1AD1M
1AD1B
1AD1I1
1AD1I11
1AD1CA
1AD1CB
1ABC
1ABB
1ABB
125 VDC
1DD1CA
1ABE
1ABA
1BBE
1BBA
120 VAC
120 VAC
120 VAC
120 VAC
120 VAC
480V MCC’s
2.75 Hr
Rating
~
~
1CD1CA
~
1CD1CB
1CD1I5
1CD1I3
~
RHR ISOLATION VALVE
Notes: First, this slide shows the T.S. rating for 1-E batteries. Then you can see the flow path of energy from the 480V buses all the way down to the 120V AC buses. Notice the small DC going into the battery. This shows the trickle charge that is maintained on the battery. It also shows how the AC is converted to DC then back to AC.

## Slide 34
1DD1CA
1DD1CB
1DD1
1BD1
1DY1B
RHR ISOLATION
VALVE
1BY1B
1BY2B
1DD11
1BD11
1BD12
1BD1M
1DD1B
1BD1B
1DD1I4
1BD1I2
1DD1I6
1BD1I12
1BD1CA
1BD1CB
1BBC
1BBA
125 VDC / 120 VAC CLASS 1E DISTRIBUTION
1BBB
1BBB
1CD1CA
1CD1CB
1ABE
1ABA
1CD1
1AD1
1CY1A
RHR ISOLATION
VALVE
1AY1A
1AY2A
1CD1M
1CD11
1AD11
1AD12
1AD1M
1CD1B
1AD1B
1CD1I3
1AD1I1
1CD1I5
1AD1I11
1AD1CA
1AD1CB
1ABA
1ABC
1ABB
1ABB
1ABF
1ABD
1ABB
1ABC
1NBO1
1ND3ACA
1ND3A
1BBE
1BBD
1BBB
1BBA
1BBF
1BBC
1NB10
1ND3BCA
1ND3B
1AB15
1AB05
1AB04
1BB06
1BB07
1BB16
1BA03
1AA02
1ND3ACB
1ND3BCB
1NB17
1NB17
1NBS
1NBI
1NBO
1NBR
1NY4N
1NY2N
1NY3N
1ND3I4
1ND3I3
1ND3I1
125 VDC
125 VDC
125 VDC
125 VDC
4160 VAC
4160 VAC
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
480 VAC SWGR
120 VAC
120 VAC
120 VAC
120 VAC
120 VAC
120 VAC
NC-TP-01942-001 LO-TP-01201-006 LO-TP-01102-012 NL-TP-01101-010
1ND3I2
1NY1N
1NYR
1NYRS
1NYS
LO-DR-01024-00

## Slide 36: 125 Volt DC Control Power
Control power for breakers is one of the loads off the 125 volt DC buses.
If DC control power was lost the breakers cannot be remotely operated and protective trips will not open the breaker.

## Slide 37
1E 125V DC INVERTER
Notes: Inverters convert DC power to AC power.

## Slide 38
1E 125V DC SWITCHGEAR ROOM

## Slide 39
1E BATTERY BANK ROOM

## Slide 40
Switchyard
13.8kV
4.16kV
480V
125VDC
120VAC
In-Plant Distribution

## Slide 41
Inverter
1ND3I3
NC
NO
NC
1NBR
1NBR
1NBS
1ND3A
Inverter
1ND3I2
1NBS
1ND3A
1NYJ
1NBS
Inverter
1ND3I4
1ND3A
1NBS
1BBC
1ABC
1NBK
1NBJ
1NBS
1NBR
1NRS
1NYC2
1NY4N
1NY1N
1NYR
1NYS
1NY2N
120V Essential AC System
Notes: Here you can talk about the interlock to prevent closing more than one supply to the

## Slide 42
120V AC CLASS 1E
1DD1CB
1DD1
1BD1
1DY1B
RHR ISOLATION
VALVE
1BY1B
1BY2B
1DD11
1BD11
1BD12
1BD1M
1DD1B
1BD1B
1DD1I4
1BD1I2
1DD1I6
1BD1I12
1BD1CA
1BD1CB
1BBC
1BBA
125 VDC / 120 VAC CLASS 1E DISTRIBUTION
1BBB
1BBB
1CD1
1CY1A
1CD1M
1CD11
1CD1B
1ABA
125 VDC
125 VDC
125 VDC
120 VAC
1AD1
1AY1A
1AY2A
1AD11
1AD12
1AD1M
1AD1B
1AD1I1
1AD1I11
1AD1CA
1AD1CB
1ABC
1ABB
1ABB
125 VDC
1DD1CA
1ABE
1ABA
1BBE
1BBA
120 VAC
120 VAC
120 VAC
120 VAC
120 VAC
480V MCC’s
1CD1CA
1CD1CB
1CD1I5
A loss of the DC input to the inverter will result in a loss of the AC output from the inverter.
~
~
1CD1I3
~
~
The power supply to the instrument bus must be manually swapped by the operator.
Notes: This slide shows the concept of how the 120V bus will be de-energized until the reg transformer is manually swapped over.

## Slide 43: Summary
Review Objectives
Any Questions?