## Slide 1
ACADs (08-006) Covered
Keywords
Technical specifications, 10 CFR50, LCO, Limiting conditions of operation, surveillance, Engineered Safety Features Actuation System (ESFAS) Instrumentation, main steam isolation, emergency feedwater actuation, auxiliary relay.
Description
Supporting Material
Plant Status
1.1.2.11 | 1.1.4.6 | 1.1.9.1.5 | 1.3.7.4 | 1.3.8.4 | 2.1.2.1 | 2.1.2.4 | 
 |  |  |  |  | 3.1.1.4 | 3.1.1.17 | 4.2.7.20
4.2.7.33 | 4.14.5 | 5.1.1.2.1.7 | 5.1.1.2.1.12c2 | 5.1.2.13.4 | 5.1.2.13.5 | 5.11.2.21 | 5.2.2.11
5.3.2.6 | 5.3.2.11 | 5.4.3.1 | 5.4.3.12 |  |  |  | 

## Slide 2
8
8
CONTAINMENT SPRAY
Equipment Cooling
Polishing
Demineralizers
8
Condensate
Pump
General System Diagram of
Palo Verde Nuclear Generating Station
Generator
LP
Turbine
HP
Turbine
LP
Turbine
LP
Turbine
MSSS
Bldg.
ADVs
MSIV
MSSVs
Refueling
Water
Tank
Containment
Building
Turbine Building
Z
MTSV
MTCV
Auxiliary Feedwater System
Safety Injection Systems
Legend::
Main Steam System
Main Feedwater System
Main Condensate System
Circulating Water System
Reactor Coolant System
Auxiliary
Building
Containment
Spray Pump
Low Pressure Safety
Injection Pump
High Pressure Safety
Injection Pump
Shutdown
Heat
Exchanger
Safety
Injection
Tank
Steam
Generator
Pressurizer
Control
Rods
Reactor
Core
Reactor
Coolant
Pump
From
Auxiliary
Feedwater
Pumps
Feedwater
Regulation
Valve
Main Feedwater
Pump
(HP)
Feedwater
Heaters
(LP)
Feedwater
Heaters
Main Condenser
Moisture Separator
Reheaters
Turbine
Bypass
Valves
Circulating
Water Pump
Cooling Tower
and Fans
Transformer
To
Switchyard
Containment Sump
PLANT STATUS!
PV Daily Status Report

## Slide 4: IT’S OUR RESPONSIBILITY!
NUCLEAR SAFETY
INDUSTRIAL SAFETY
RADIOLOGICAL SAFETY
SAFETY CULTURE

## Slide 6
Technical Specifications
Upgraded Final Safety Analysis Report (UFSAR)
Tech Spec Basis
10CFR
Limiting Condition for Operation (LCO)
Operating License

## Slide 7: "The Operating License"
The NRC will issue a license for a reactor when it has reasonable assurance that the public health and safety will be adequately protected during operation of that reactor.
A license is issued for 40 years.
Technical Specifications are an appendix to our license, and
Our license is conditional on us meeting tech specs
Responsibilities

## Slide 8: Tech Specs
Define Safety Limits
Place time limits on degraded operation.
Place mandatory surveillance requirements on equipment.
Define design features of the plant.
Designate administrative controls related to plant operations and surveillance requirements.

## Slide 9: If we don’t meet the LCO and cannot take the necessary actions, then we must shut down or stop the activity

## Slide 10
However, there is an exception:
10 CFR 50.54X states:
A licensee may take reasonable action that departs from a license condition or a Technical Specification in an emergency when this action is immediately needed to protect the public health and safety and no action consistent with license conditions and Technical Specifications that can provide adequate or equivalent protection is immediately apparent.
10CFR50.54X requires prior approval by a licensed senior operator

## Slide 11: The 5 Sections of Tech Spec
1. Use & Applications: definitions, completion times & frequencies, & logic
2. Safety Limits: pressure & DNBR limits, peak fuel centerline temp
3. Limiting Conditions for Operation: the longest section, and the one we are most concerned with in I&C
4. Design Features: calls out design criteria such as maximum fuel enrichments, Spent Fuel Pool design
5. Administrative Controls: dictates organizational structure and responsibilities, CR staffing, requirement for procedures, OT limits, ANSI 3.1 requirements, defines high radiation areas, record keeping and many other administrative requirements.

## Slide 12: Definition of an LCO: (from 10 CFR 50.36)
Limiting conditions for operation are the lowest functional capability or performance levels of equipment required for safe operation of the facility.

## Slide 13: LCO Logical Connectors
Trip and verify or Reduce and Perform…..

## Slide 15: When do you enter an LCO? When do you exit?
You enter an LCO upon discovery that the required conditions are not met
Completion time is the time allowed for completing a required action referenced to the time of discovery.
You exit the LCO when the conditions for entry are no longer met

## Slide 16: 3.0.3, The General LCO
TS 3.0.3-When an LCO is not met and the associated ACTIONS are not met, an associated ACTION is not provided, or if directed by the associated ACTIONS, the unit shall be placed in a MODE or other specified condition in which the LCO is not applicable

## Slide 17: Surveillance Requirements
"Surveillance requirements are requirements relating to test, calibration, or inspection to assure that the necessary quality of systems and components is maintained, that facility operation will be within the safety limits, and that the limiting conditions of operation will be met."

## Slide 18: Tech Specs Relating to ESFAS
Section 3.3, Instrumentation
  3.3.5 Engineered Safety Features Actuation System (ESFAS) Instrumentation
  3.3.6 ESFAS Logic and Manual Trip
  3.3.7 Diesel Generator (DG) -- Loss of Voltage Start (LOVS)
  3.3.8 Containment Purge Isolation Actuation Signal (CPIAS)
  3.3.9 Control Room Essential Filtration Actuation Signal (CREFAS)
ESFAS systems are very interconnected, and there are other tech specs affected

## Slide 19: Tech Specs Relating to ESFAS
Section 3.7, Plant Systems
  3.7.11 Control Room Essential Filtration (CREFS) System
  3.7.12 Control Room Emergency Air Temperature Control System (CREATCS)
  3.7.13 Engineered Safety Feature (ESF) Pump Room Exhaust Air Cleanup System (PREACS)
ESFAS systems are very interconnected, and there are other tech specs affected

## Slide 20: Standard Format for an LCO
Condition | Required Action | Comletion Time
A. This is what is inoperable | A.1 This is what you have to do | This is how long you have to do it
B. This is what else is inoperable | B.1 This is what else you have to do | This is how long you have to do it
3.3 Section
3.3.10 Title of the LCO
LCO 3.3.10 This is the condition we must maintain
Applicability:
Actions:
This is when, or what plant mode applies to this condition

## Slide 21: Look at 3.3.5 and 3.3.6
Specifically refers to NSSS ESFAS
Four ESFAS trip and bypass removal channels for each function in Table 3.3.5-1 shall be OPERABLE.
If one channel is out, place that channel in trip OR bypass within 1 hour
If two channels out, place one in bypass and the other in trip within 1 hour

## Slide 22: The two books that are used with the Technical Specifications
Tech Specs are about 345 pages long
Technical Specification Basis Document – does not drive plant operations, only explains our interpretation of Tech Specs. 853 pages long
Technical Requirements Manual – contains other requirements not in our license

## Slide 23: Tech Spec Zones

## Slide 24: ENGINEERed SAFETY FEATURES ACTUATION SYSTEM
Course Terminal Objective:
Given the appropriate references, the participant will be able to describe the purpose, operation, and maintenance of the Engineered Safety Features Actuation System. The participant will demonstrate mastery of the material by achieving a score of 80% or greater on a written examination at the end of the course.

## Slide 25: ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)
Enabling Objectives:
E001 IDENTIFY THE SAFETY SYSTEMS CONTROLLED BY THE AUXILIARY RELAY CABINET.
E002 DESCRIBE THE GENERAL LAYOUT AND CODING SYSTEM ASSOCIATED WITH THE AUXILIARY RELAY CABINETS.

## Slide 26
E003 DESCRIBE THE CONDITIONS NECESSARY TO INITIATE THE SAFETY SYSTEM.
E004 GIVEN A TYPICAL TRIP CIRCUIT DIAGRAM, EXPLAIN THE OPERATION OF THE CIRCUIT FOR NORMAL, TRIP, RESET AND TEST CONDITIONS.
E005 EXPLAIN SAFETY SYSTEM TRIP CIRCUITS THAT EMPLOY INTERPOSING RELAYS.
ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)

## Slide 27
E006 DESCRIBE THE OPERATION OF THE EFAS ACTUATION FROM THE CIRCUIT LOGIC TO THE ACTUATED DEVICES.
E007 GIVEN AN ESFAS TEST CIRCUIT DIAGRAM AND A FRONT PANEL DRAWING OF THE ESFAS TEST MODULE, DESCRIBE THE OPERATION OF THE TEST CIRCUITS.
E008 DESCRIBE THE SURVEILLANCE TESTS ASSOCIATED WITH ESFAS.
ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)

## Slide 28: ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)
EO09 Describe the use of Prevent Event Tools and Electrical Safe Work Practices to minimize human performance errors during testing or maintenance of the NSSS ESFAS.
EO10 Given examples of NSSS ESFAS maintenance problems, determine the fault using procedures, NSSS ESFAS prints, Tech Manuals, and applicable documents .

## Slide 29: O.E.
OE: Human Error Results in Technical Specification Violation Due to Two RPS Channels Out-of-Service During Surveillance Testing at Calvert Cliffs.
Contrary to procedure, test equipment was installed out of sequence resulting in a containment pressure high signal on one channel, then slide links were opened in the wrong cabinet taking another channel out of service. Control room operators reacted promptly to the indications this caused in the control room and properly deduced that operations were being performed on the wrong train. The technicians were promptly notified resulting in both channels being simultaneously out of service for approximately 15 seconds. This event is noteworthy for the human performance errors that adversely affected the reactor protection system.
Human performance errors included performing two steps of the procedure out of sequence and inadequate self checking resulting in work in the wrong ESFAS cabinet.

## Slide 30: Prevent Events
What are the critical steps of the task I’m going to perform? What document describes it? Do I understand it?
What is the worst thing that can happen and how can I prevent it?
What else could go wrong?
What are the safety and / or radiation protection considerations?
Is my training and are my qualifications up to date?

## Slide 31: FUNCTIONS
Extension of the Plant Protections System (PPS)
Provide initiating signals for ESF components which require automatic actuation following a rupture of a primary or secondary (I.E. LOCA, Main Steam OR Feedwater Line Break)
Interface between the PPS Cabinets and the plant equipment comprising the ESFAS
Pg. 2

## Slide 32
Pg. 3

## Slide 33
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
RAS
RAS
MSIS
CSAS
CIAS
EFAS-1
SIAS
RAS
EFAS-2
STEAM GENERATOR RUPTURE CIRCUIT
LOCATED OUTSIDE CONTAINMENT
Analog
Analog
Analog
Analog
Analog
Analog
Analog
Variable
Variable
Variable
RWT
LVL
Steam Generator
WR
LVL
NR
LVL
Press
Press
Containment
Pressurizer
Press

## Slide 34
Analog Bi-Stable
Hi S/G #1 Level
Hi S/G #2 Level
Hi Cont. Press.
Hi-Hi Cont. Press.
Low S/G #1 Level
Low S/G #2 Level
Low RWT Level
Plant Computer
100 mSec Time Delay
Turns Off on Trip
Turns Off on Trip
Hysteresis Loop raises or lowers comparator voltage by 100 mV for reset differential
Pg. 5

## Slide 35
Variable Input Trip Bi-Stable
Low Pressurizer Press. Low S/G # 1 Press. Low S/G # 2 Press.
From Variable Setpoint Card
From Variable Setpoint Card
Pg. 7

## Slide 36
Variable Input Trip Bi-Stable
Low Pressurizer Pressure Trip
The low PZR PRESS trip is provided with a variable setpoint nominal setting of 1837 psia and a floor of 100 psia.
During plant shutdown and cooldown evolutions, the operator can manually reset the trip setpoint.
Depressing the reset push button (PB) will lower the trip setpoint to 400 psi below existing pressure. This allows the operator to avoid the safety injection actuation and containment isolation actuation signals (SIAS/CIAS) that would normally accompany plant de-pressurization since these ESFAS functions are actuated by the same low pressurizer pressure bistable that causes a reactor trip.
Trip setpoint reset may continue down to a floor of 100 psia, but:
10 seconds must elapse between setpoint resets. Otherwise, no reset function will occur.
Each reset will not result in a full 400 psi decrease in setpoint but will only decrease it to 400 psi below existing pressure.
When actual pressure is below 400 psia, the operator can manually bypass this trip. The bypass will automatically be removed if pressure rises above 500 psia.
The trip setpoint will automatically increase as system pressure increases. During the increase, setpoint pressure will lag existing system pressure by a fixed increment of 400 psi until the nominal setpoint of 1837 psia is reached.
Should a channel trip actually occur, the reset is ineffective until pressure recovers above the trip setpoint.
Pre-trip alarms are provided at 43 psi above the existing trip setpoint.

## Slide 37
Variable Input Trip Bi-Stable
Low Steam Generator Pressure Trip
The low SG PRESS trip is another variable setpoint trip. Nominal setpoint is 960 psia. Separate trips are provided for each SG.
Setpoint variation is similar to that of the low pressurizer pressure trip with the following exceptions:
Manual setpoint reset will reduce trip setpoint to 200 psi below existing pressure.
There is no setpoint floor: i.e., setpoint reduction may continue to 0 psia, eliminating the need for an operating trip bypass.
As SG pressure increases, the fixed increment between actual and setpoint pressure is 200 psi. Pretrip alarms are provided at 28 psi above trip setpoint pressure.

## Slide 38
Differential Bi-Stable
Pg. 9

## Slide 39
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
RAS
RAS
MSIS
CSAS
CIAS
EFAS-1
SIAS
RAS
EFAS-2
STEAM GENERATOR RUPTURE CIRCUIT
LOCATED OUTSIDE CONTAINMENT
Analog
Analog
Analog
Analog
Analog
Analog
Analog
Variable
Variable
Variable

## Slide 40
Loss of Coolant Accident
Low Pressurizer Pressure – 1837 psia or 3.0# – Containment
SIAS –
High-High Containment Pressure – 8.5#
CSAS –
Low Refueling Water Tank Level – 9.4%
RAS –
When a Loss of Coolant Accident occurs a Reactor Trip and a Safety Injection Actuation Signal will be generated on a Low Pressurizer Pressure or high containment pressure. A Containment Spray Actuation Signal will be generated on a High-High Containment Pressure. A Recirculation Actuation Signal will be generated on a Low Refueling Water Tank level
If Offsite power is NOT available, the Safety Injection Tanks will REFLOOD the core as the Emergency Diesel Generators start and supply power to the Class Buses as pressure gets down to 600#. All of the Safety Injection Pumps will start and the High Pressure and Low Pressure Safety Injection Pumps will put water from the Refueling Water Tank into the core at ~1800# and ~200# respectively and REFILL the core.
The Containment Spray Actuation Signal will cause spray flow to initiate. When the Recirculation Actuation Signal is received the Containment Sump Outlet Valve will open and the suction for the High Pressure Safety Injection Pump and the Containment Spray Pump will shift to Containment effectively putting Containment on RECIRC. The Low Pressure Safety Injection Pump will stop.
#1
Steam
Generator
PZR
Heaters
Aux Spray
Safety
Valve
(4)
Steam
Generator

## Slide 41: Reactivity Management
SAFETY INJECTION SYSTEM
HPSI/LPSI Pumps
    Injects borated water from the Refueling Water Tank
    Negative reactivity addition
ESSENTIAL FEEDWATER SYSTEM
Essential Feedwater Pumps
    Injects cool water from the Condensate Storage Tank
    Positive reactivity addition

## Slide 42
Safety Injection System
Refueling
Water
Tank
.
The spray nozzles are designed to disperse the water throughout Containment in the form of droplets to increase the heat transfer surface area. Nozzles are located in the dome and at other levels inside containment.
The design basis for the Containment Spray System is that it must reduce the Containment pressure by ½ in 24 hours. The Containment Building is rated for 60 psig.
SIAS – 1837 psia or 3# in Containment
CSAS - Hi-Hi Cont. Press. 8.5#
RAS – Low RWT Level – 9.4%
To Reactor Cold Leg
Shutdown Cooling Line
Pg. 11

## Slide 43: Safety Systems Descriptions
Safety Injection Actuation Signal (SIAS):
  Actuates the Safety Injection System to inject cool borated water into the RCS to mitigate fuel damage that could be caused by a Loss of Coolant Accident (LOCA)
Pg. 11

## Slide 44: SAFETY INJECTION ACTUATION SYSTEM (SIAS)
SIAS will be generated at both decreasing pressurizer pressure of 1837 psia (ceiling-variable setpoint) and increasing high containment pressure of 3.0 psig
The low pressurizer pressure function also trips the reactor via the RPS.
The high containment pressure actuation is also shared with the corresponding reactor trip.
Pre-trip alarms are provided to alert the operator that a trip value is being approached.

## Slide 45: SAFETY INJECTION ACTUATION SYSTEM (SIAS)
SIAS is required in the event of a loss of coolant accident (LOCA), main steam line break (MSLB), or steam generator tube rupture (SGTR).
SIAS actuates the components required for injection of borated water into the reactor coolant system and emergency core cooling, thereby ensuring adequate shutdown margin and minimizing core fuel damage.

## Slide 46: SAFETY INJECTION ACTUATION SYSTEM (SIAS)
The Safety Injection System receives CIAS, CSAS, RAS and SIAS signals from the ESFAS to start/stop SI system pumps and open/close SI system valves. PPS ESFAS starts the pumps by sending a signal to BOP-ESFAS which in turn directly starts the pumps. Automatic SI valves receive their signals directly from PPS ESFAS via the Auxiliary Relay cabinets.

## Slide 47: Safety Systems Descriptions
Containment Isolation Actuation Signal (CIAS):
  Actuates Containment Isolation System to provide isolation of fluid system lines that penetrate Containment in order to confine any radioactivity to Containment
Pg. 12

## Slide 48: CONTAINMENT ISOLATION ACTUATION SYSTEM (CIAS)
A CIAS is also generated on either low pressurizer pressure or high containment pressure.
The setpoints and actuation functions are the same as those for SIAS and the corresponding RPS trips.
A SIAS, CIAS and reactor trip will occur simultaneously.
Pre-trip alarms are provided; low PZR pressure pre-trip at 1880 psia; high containment pressure pretrip 2.5 psig.

## Slide 49: CONTAINMENT ISOLATION ACTUATION SYSTEM (CIAS)
The CIAS initiates isolation of selected process lines penetrating the containment.
By isolating the containment: The release of radioactive material to atmosphere is minimized for accidents involving fuel damage and the associated fission product releases.
Energy release to the containment that could lead to over pressurization and potential failure is limited in the event of main feedwater or steam system piping ruptures.

## Slide 50: Safety Systems Descriptions
Containment Spray Actuation Signal (CSAS):
  Actuates the Containment Spray System to initiate the spraying of cool borated water to remove heat from the Containment atmosphere that could be caused by a Loss of Coolant Accident (LOCA) or a Steam Line Break (HELB)
Pg. 12

## Slide 51: CONTAINMENT SPRAY ACTUATION SYSTEM (CSAS)
CSAS will be initiated on an increasing (HI-HI) containment pressure of 8.5 psig.
CSAS occurs at a higher containment pressure than the SIAS & CIAS actuations
Both SIAS & CIAS should also be present during any containment spray actuation.
Pre-trip alarms are provided at 6.0 psig.
CSAS actuates the containment spray systems in the event of a LOCA or MSLB.
The cool borated spray water removes heat from the containment atmosphere to limit and reduce post accident containment pressure.

## Slide 52: Safety Systems Descriptions
Recirculation Actuation Signal (RAS):
  Actuates the Recirculation System to change the suction of the Safety Injection and Containment Spray pumps from the Refueling Water Tank to the Containment Sump
Pg. 13

## Slide 53: RECIRCULATION ACTUATION SYSTEM (RAS)
RAS will be generated on a decreasing refueling water tank (RWT) level of 9.4%.
Pre-trip alarms are provided at 11% RWT level.
The RAS is provided to initiate recirculation of borated water from the containment sump.
This provides for long term post-accident recirc and cooling
Following SIAS actuation, the RWT serves as the source of borated water emergency core cooling using the safety injection system for core injection and containment spray.
When the RWT water inventory is depleted, a RAS will cause the ESF systems to automatically shift their suction to the containment sump.
The sump, being full of water previously pumped from the RWT for core injection and containment spray, can now serve as the borated water supply for long term core cooling.

## Slide 54
Main Steam Safety Valves
Excessive Steam Demand - Downstream
MSIS – Low Steam Generator Pressure – 960#
#1
Steam
Generator
PZR
Heaters
Aux Spray
Steam
Generator
When an Excessive Steam Demand occurs a Reactor Trip and a Main Steam Isolation Signal will be generated.
A Main Steam Isolation Signal will close the Main Steam Isolation Valves and the Feedwater Isolation Valves and the event will essentially be terminated. The Atmospheric Dump Valves and Auxiliary Feedwater Flow will be used for heat removal.

## Slide 55
Excessive Steam Demand - Upstream
Main Steam Safety Valves
MSIS - Low Steam Generator Pressure – 960#
SIAS – Low Pressurizer Pressure – 1837 psia
CSAS – High Containment Pressure – 8.5#
If the Excessive Steam Demand is inside Containment then a Containment Spray Actuation Signal will be generated. The Reactor Coolant Pumps will be secured and the plant will go on Natural Circulation.
#1
Steam
Generator
PZR
Heaters
Aux Spray
Safety
Valve
(4)
Steam
Generator
When an Excessive Steam Demand occurs Upstream of the Main Steam Isolation Valves a Reactor Trip, a Main Steam Isolation Signal, and a Safety Injection Actuation Signal will also be generated.
A Main Steam Isolation Signal will close the Main Steam Isolation Valves and the Feedwater Isolation Valves but the event will not be terminated until the faulty Steam Generator boils dry. When this occurs the Atmospheric Dump Valves and Auxiliary Feedwater Flow will be used for heat removal on the good Steam Generator to stabilize the plant.

## Slide 56: Safety Systems Descriptions
Main Steam Isolation Actuation Signal (MSIS):
  Actuates the Main Steam Isolation System to isolate a Steam Generator due to a ruptured steam line, feedwater line or a high level condition to assure that a heat sink is maintained in the unlikely event of a large Steam Line or Feedline break.
Pg. 16

## Slide 57: MAIN STEAM ISOLATION ACTUATION SYSTEM (MSIS)
MSIS will be generated by the ESFAS when any of the following conditions occur:
A decreasing SG No. 1 or SG No. 2 pressure of 895 psia (ceiling - variable setpoint)
An increasing level in SG No. 1 or SG No. 2 level of 91.0% (NR)
An increasing containment pressure of 3.0 psig. All inputs are shared with the corresponding RPS reactor trips.
Pre-trip alarms are provided for all inputs:
Low SG press pre-trip 923 psia
HI SG level pre-trip 88.6%
High containment press pre-trip 2.5 psig

## Slide 58: MAIN STEAM ISOLATION ACTUATION SYSTEM (MSIS)
MSIS will isolate the main steam, main feedwater, sample and blowdown lines on both steam generators regardless of which SG (if either) was responsible for the actuation.
In the event of a MSLB, the MSIS will limit the energy release to containment and prevent excessive containment pressures.
By isolating both steam generators, only the damaged SG can release its energy. It also prevents a complete blow-down of both SG’s and the resulting loss of heat sink for the reactor core.

## Slide 59
They provide overpressure protection for the Steam Generators. The valves have varying setpoints with the first one set ~ 1250#. Together they can relieve >100% steam flow.
Designed to close within 5 seconds in an emergency, Main Steam Isolation Signal (MSIS). There are two separate class hydraulic operating trains to ensure they will close.
There are a total of 8 Steam Bypass Control Valves, 6 go to the Main Condenser, 2 go directly to the atmosphere. They open automatically if the Turbine Trips during normal operation. The 2 to atmosphere can be used if the condenser is unavailable and having them go directly to atmosphere also protects the condenser from too much steam flow if all 8 valves opened at once and the turbine was still partially loaded.
Main Steam Safety Valves
Receive an open signal of an Auxiliary Feedwater Actuation Signal (AFAS). The steam is used to drive a turbine that provides the rotation for the pump on the other end of the shaft. This pump is a key component in protecting the plant from a Loss of All Feedwater accident (LOAF).
Atmospheric Dump Valves
Auxiliary Feedwater
Main Steam Isolation Valves
Main Feed Pumps
SBCV’s
Main Turbine Stop & Control Valves
They are opened by a control room operator to remove heat when the Main Condenser or Steam Bypass Control Valves are not available. They are plug type valves with stacked discs that are etched for even flow characteristics as the valves open. They are normally air operated to open and spring shut, but they have a backup nitrogen system for emergency operation.
MAIN STEAM SYSTEM
Pg. 14

## Slide 60
Main Feedwater System
Steam driven, 1-stage, 50% capacity, horizontal, centrifugal pumps. The pumps have a mini-flow line for recirculation to prevent them from overheating when operating near shutoff head. They receive steam from Main Steam or Hot Reheat depending on how much steam flow is flowing through the Main Turbine.
U-tube heat exchangers with feedwater in the tubes and extraction steam from the High Pressure Turbine is on the outside of the tubes, or in the shell.
Feedwater
Isolation
Valves
Feedwater
Regulating
Valves
Designed to close on a Main Steam Isolation Signal
Pg. 15

## Slide 61
Auxiliary Feedwater System
There are 2 electric driven pumps and 1 steam driven pump. All 3 pumps are 8-stage, horizontal, centrifugal pumps, powered from class power, tech spec related. One electric pump (AFB) and the steam driven pump (AFA) are designated as Essential. The other electric pump is called the Non-Essential Auxiliary Feedwater Pump (AFN). Both electric pumps are powered from the class 4160 busses, AFB from PBB-SO4 and AFN from PBA-SO3. The steam driven pump is designed to be able to supply water to the Steam Generators during a Station Blackout when there is no power available to the Class A/C busses. Class DC will be available for the steam supply and discharge valves. The pumps can put out about 1000 gpm and shutoff head is ~ 1425#.
The Isolation and Regulating Valves are used to isolate and control the flow from the Auxiliary Feedwater Pumps to the Steam Generators. They will cycle open and close on an Auxiliary Feedwater Actuation Signal.
The Condensate Storage Tank stores 550,000 gallons of pure makeup water for the Steam Generators, 330,000 is reserved for Auxiliary Feedwater. A nitrogen cover blanket is used to minimize the amount of oxygen in the water.
The functions of the AFW System are:
Provide feedwater to the Steam Generators during startup, shutdown and cooldown of the Reactor Coolant System .
Provide feedwater to the Steam Generators during emergency operations when the Main Feedwater System is unavailable.
The Auxiliary Feedwater System is designed to feed the S/G’s when level drops to ~ 25%, generating a Reactor Trip and an Aux Feedwater Actuation Signal (AFAS). The AFAS starts the Essential Auxiliary Feedwater Pumps and opens the isolation and regulating valves to the affected S/G. The lines tap in downstream of the Downcomer Feedwater Isolation Valves. When level reaches ~ 40%, the signal will reset and feed will be isolated to the Steam Generators.
Pg. 17

## Slide 62: Safety Systems Descriptions
Emergency Feedwater Actuation Signal (EFAS):
  Actuates the Emergency Feedwater System to fill a Steam Generator(s) from the Condensate Storage Tank except when it is determined that the low level was caused by a Steam Generator rupture.
Pg. 18

## Slide 63: EMERGENCY FEEDWATER ACTUATION SYSTEM (EFAS1/EFAS2)
Separate AFAS signals are developed for each steam generator: AFAS-1 for SG-1 and AFAS-2 for SG-2.
An AFAS will be initiated for a particular steam generator when it has a decreasing level of 25.8% WR.
The SG pressure instrumentation channels are compared in the AFAS circuitry.
As long as pressures in both SGs are about equal, both will be considered intact.
If pressure in the two SGs differs by more than 185 psi, the one with the lower pressure will be considered ruptured and will not receive an AFAS actuation.

## Slide 64: EMERGENCY FEEDWATER ACTUATION SYSTEM (EFAS1/EFAS2)
The AFAS will start the auxiliary feedwater pumps and open the auxiliary feedwater valves to the intact steam generator, maintaining a minimum water inventory for decay heat removal.
This provides protection for a loss of normal feedwater flow.
Under certain conditions, the actuation signal may be initiated by the diverse auxiliary feedwater actuation system (DAFAS)
Once actuated, the auxiliary feedwater pumps will remain operating until the actuation has been reset and the pumps manually secured.
The actuated valves will cycle open and shut automatically (open @ 25.8% WR, close @ 40.8% WR) to maintain level in the appropriate S/G. Each auxiliary feedwater train can feed either SG individually or both SGs simultaneously.

## Slide 68
Pg. 19

## Slide 69
A
B
NID18 NSSS ESFAS

## Slide 70: ESFAS Circuit Description
SIAS, CIAS, RAS and CSAS are identical circuits with their PPS Initiation Relay contacts in series
EFAS-1, EFAS-2 and MSIS differ in that their circuits include Interposing Relays and have their PPS Initiation Relay contacts in parallel
Regardless of the Initiation Relay contact arrangement, any ESFAS actuation requires a select 2 of 4 logic
Pg. 20

## Slide 71
Pg. 20

## Slide 76
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
RAS
RAS
MSIS
CSAS
CIAS
EFAS-1
SIAS
RAS
EFAS-2
STEAM GENERATOR RUPTURE CIRCUIT
LOCATED OUTSIDE CONTAINMENT
Analog
Analog
Analog
Analog
Analog
Analog
Analog
Variable
Variable
Variable

## Slide 77
2/4
2/4
REMOTE
MANUAL
REMOTE
MANUAL
SG-1
LEVEL
SG-2
LEVEL
SG-2 > SG-1 PRESS
SG-1 > SG-2 PRESS
N001-13.06-59
And Gate “A”
And Gate “B”
And Gate “C”
And Gate “D”
Or Gate
Or Gate
Not
Gate “A”
Not
Gate “B”
EFAS - 1
EFAS - 2
Pg. 22

## Slide 79
Pg. 24

## Slide 81
M
M
SG 1
SG 2
HV-33
HV-32
UV-37
UV-36
HV-31
HV-30
UV-35
UV-34
AUXILIARY FEEDWATER PUMP (TURBINE DRIVEN)
AFA-P01
AUXILIARY FEEDWATER PUMP (MOTOR DRIVEN)
AFB-P01
SG-1
SG-2
UV134
UV138
REG VALVES: HV-30, 31, 32 and 33
ISOLATION VALVES: UV-34, 35, 36 and 37
M
M
M
M
M
M
CONDITION 1
Pg. 26

## Slide 82
M
SG 1
SG 2
HV-33
HV-32
UV-37
UV-36
HV-31
HV-30
HU-35
UV-34
AUXILIARY FEEDWATER PUMP (TURBINE DRIVEN)
AFA-P01
AUXILIARY FEEDWATER PUMP (MOTOR DRIVEN)
AFB-P01
SG-1
SG-2
UV134
UV138
REG VALVES: HV-30, 31, 32 and 33
ISOLATION VALVES: UV-34, 35, 36 and 37
M
M
M
M
CONDITION 2
RUPTURED
M
M
M
Pg. 27

## Slide 83
M
SG 1
SG 2
HV-33
HV-32
UV-37
UV-36
HV-31
HV-30
UV-35
UV-34
AUXILIARY FEEDWATER PUMP (TURBINE DRIVEN)
AFA-P01
AUXILIARY FEEDWATER PUMP (MOTOR DRIVEN)
AFB-P01
SG-1
SG-2
UV134
UV138
REG VALVES: HV-30, 31, 32 and 33
ISOLATION VALVES: UV-34, 35, 36 and 37
M
M
M
CONDITION 3
RUPTURED
M
M
M
M
Pg. 28

## Slide 87
BAY 4
BAY 3
BAY 2
BAY 1
BAY 5
BAY 6
BAY 7
BAY 8
PS51
PS61
PS71
PS81
120 Vac Vital Power Channel “A”
120 Vac Vital Power Channel “A”
120 Vac Vital Power Channel “B”
120 Vac Vital Power Channel “B”
“A” TRAIN ESFAS BAYS
Bays 3, 4, 5 and 6 comprise the 1-3 trip leg
PS 51 & PS61 service trip legs in Bays 3, 4, 5, & 6
Bays 1, 2, 7 and 8 comprise the 2-4 trip leg
PS 71 & PS81 service trip legs in Bays 1, 2, 7, & 8
FIREWALL
N001-13.06-64
Interposing Relays
Interposing Relays
Test Module
Control Panel
Control Panel
Subgroup Rotary Relays
Subgroup Rotary Relays
Subgroup Rotary Relays
Subgroup Rotary Relays
Ground Det
Ground Det
Pg. 29
XJ-SAA-EY-47
XJ-SAA-EY-48
XJ-SAA-EY-49
XJ-SAA-EY-50

## Slide 88
BAY 4
BAY 3
BAY 2
BAY 1
BAY 5
BAY 6
BAY 7
BAY 8
PS51
PS61
PS71
PS81
120 Vac Vital Power Channel “C”
120 Vac Vital Power Channel “C”
120 Vac Vital Power Channel “D”
120 Vac Vital Power Channel “D”
“B” TRAIN ESFAS BAYS
Relays K4XX
TB41 – TB48
Relays K3XX
TB31 – TB38
Relays K2XX
TB21 – TB28
Relays K1XX
TB11 – TB18
TB81 – TB89
Relays K7XX
TB71 – TB79
Relays K6XX
TB61 – TB69
TB51 – TB59
Coding:
1st digit of the reference designation defines the bay within which the component is located for terminal boards and relays.
Rear
Front
Subgroup Rotary Relays
Subgroup Rotary Relays
Subgroup Rotary Relays
Subgroup Rotary Relays
Interposing Relays
Interposing Relays
Ground Det
Control Panel
Control Panel
Test Module
Ground Det
Pg. 30
XJ-SAB-EY-51
XJ-SAB-EY-52
XJ-SAB-EY-53
XJ-SAB-EY-54

## Slide 89: Bay 3
Notes: Bay 3 Relays

## Slide 90
Bay 8
Lockout Relays
Test Relays
Suppression Diodes (Beneath Cover)

## Slide 91
Interposing Relays
Lockout Relays

## Slide 93: Power Supply Input Breaker
Notes: Power Supply Input Breaker

## Slide 94
Fault Protection Circuit
PS 51
R54
C51
CR53
Q51
CR52
+
-
POWER SUPPLIES
Lambda Supplies
120 VAC input
36VDC output
Overload Protection
Thermal
Current limiting circuit
Fuses
Fault Protection:
Overvoltage protection circuit
Clamping circuit limits or shorts any AC faults
  CR52 clamps negative cycle
  CR53 & Q51 clamp positive cycle
Q51
CR52
Sh.13 N001-1306-80
Pg. 34

## Slide 95
Ground on the negative line
Ground on the positive line
Ground Detection Module
VTM page 11-1
#118 & #129 0f 149
Bays
5 & 8
Only
Q4 Comparator
Trip Relay
Trip Relay
Q1 Comparator
+ GND Light
- GND Light
Pg. 36

## Slide 96
K_1 Relay
DS_1 Indicator
Shunt Test Jacks
Ground Detector
DC Power Supply Assembly
N001-1306-80
Sheet 13
CR_1 Diode
Power Supply Breaker
Q_1

## Slide 97
Pg. 37

## Slide 98
Individual Relay Test Circuit
LK2
LK2
LK2
AK1
AK1
AK1
AK1

## Slide 99
Pin 1 +24Vdc
Annunciator Assemblies
Bay 6
&
Bay 7
8 Identical Circuits
U1
Opto-isolator
LED
Normal
U1 conducting
Q1 conducting
K1 energized
Pg. 39

## Slide 100: Bay 6/7 Control Panel
Power On
Indicators
Lockout Reset PB’s
Manual Trip PB’s
Power Circuit Breakers
Blown Fuse Indicators
Bypass Test
Indicators
Pg. 40

## Slide 102: Surveillance Testing
36ST-9SA01
ESFAS TRAIN “A” SUBGROUP RELAY FUNCTIONAL TEST
Verifies the Train “A” ESFAS automatic actuation subgroup relays and associated equipment actuation circuits operate properly. Subgroup relays are tested one at a time.
At least every 9 months, staggered with 36ST-9SA02
Required in modes 1 through 4 for SIAS, CIAS and RAS relays. Required in mode 1 through 3 for CSAS, MSIS, AFAS-1 and AFAS-2.
Relays exempt from testing during power operations shall be tested every 18 months by 36ST-9SA03
Pg. 41

## Slide 103: Surveillance Testing
36ST-9SA02
ESFAS TRAIN “B” SUBGROUP RELAY FUNCTIONAL TEST
Verifies the Train “B” ESFAS automatic actuation subgroup relays and associated equipment actuation circuits operate properly. Subgroup relays are tested one at a time.
At least every 9 months, staggered with 36ST-9SA01
Required in modes 1 through 4 for SIAS, CIAS and RAS relays. Required in mode 1 through 3 for CSAS, MSIS, AFAS-1 and AFAS-2.
Relays exempt from testing during power operations shall be tested every 18 months by 36ST-9SA04

## Slide 104: Surveillance Testing
36ST-9SA03
ESFAS TRAIN “A” SUBGROUP RELAY SHUTDOWN FUNCTIONAL TEST
Verifies the Train “A” ESFAS automatic actuation subgroup relays and associated equipment actuation circuits, which are not tested during power operations, operate properly
At least every 18 months, but is designated as “N” (as required) during REFUELING, staggered with 36ST-9SA04
Required for modes 1 through 4

## Slide 105: Surveillance Testing
36ST-9SA04
ESFAS TRAIN “B” SUBGROUP RELAY SHUTDOWN FUNCTIONAL TEST
Verifies the Train “B” ESFAS automatic actuation subgroup relays and associated equipment actuation circuits, which are not tested during power operations, operate properly
At least every 18 months, but is designated as “N” (as required) during REFUELING, staggered with 36ST-9SA03
Required for modes 1 through 4

## Slide 106: Surveillance Testing
36ST-9SB04
PPS FUNCTIONAL TEST – RPS/ESFAS LOGIC
Verifies the RPS & ESFAS Trip Paths and Matrix Logic are OPERABLE.
Quarterly
Required for modes 1 through 4

## Slide 107: Surveillance Testing
73ST-9DG01 (Train A)/73ST-9DG02 (Train B)
CLASS 1E DIESEL GENERATOR AND INTEGRATED SAFEGUARDS TEST
Performance of these procedures satisfies all of the requirements for the Subgroup Relay Functional Tests:
73ST-9DG01 satisfies: 36ST-9SA01 and 36ST-9SA03
    73ST-9DG02 satisfies: 36ST-9SA02 and 36ST-9SA04
Testing frequency is every 18 months
Mode applicability 1 through 4
Any subgroup relay that fails during the performance of the test will be tested per the Subgroup Relay Shutdown Functional Test:
    73ST-9DG01: tested under 36ST-9SA03
    73ST-9DG02: tested under 36ST-9SA04

## Slide 108
System Interfaces
Reactor coolant (RC)
The RC system provides pressurizer pressure inputs to the PPS.
The pressurizer pressure signal is used in the low pressurizer pressure reactor trip as well as the SIAS and CIAS actuations.
Main steam (SG)
Each steam generator provides two water level signals to the PPS to be used as PPS bistable inputs. The SG wide range (WR) signals are used for the low steam generator water level reactor trip and auxiliary feedwater actuation system (AFAS) actuations. The SG narrow range (NR) signals are used for the high steam generator water level reactor trip and main steam isolation system (MSIS) actuations.
Pressure signals from each SG are also provided as inputs. These signals are used for the low steam generator pressure reactor trip, AFAS SG rupture logic and main steam isolation system (MSIS) actuations.
Auxiliary feedwater system (AF)
The AF system receives auxiliary feedwater actuation system (AFAS-1 and AFAS-2) and safety injection actuation system (SIAS) signals from the ESFAS.
Chemical & volume control system (CH)
The CH system receives containment isolation actuation system (CIAS), containment spray actuation system (CSAS) and SIAS signals from the ESFAS.
Containment purge system (CP)
The CP system receives CIAS signals from the ESFAS.
Condensate transfer system (CT)
The CT system receives AFAS and SIAS signals from the ESFAS.
Diesel generator system (DG)
The DG system receives AFAS, SIAS and CSAS signals from the ESFAS.
Safety equipment status system (ES)
The ES system receives AFAS, CIAS, CSAS, MSIS, RAS and SIAS signals from the ESFAS.
Essential cooling water system (EW)
The EW system receives a SIAS signal from the ESFAS.
Service gas system N2 & H2 (GA)
The GA system receives a CIAS signal from the ESFAS.
Gaseous radwaste system (GR)
The GR system receives a CIAS signal from the ESFAS.
HVAC - auxiliary building (HA)
The HA system receives AFAS, CSAS and SIAS signals from the ESFAS.
Pg. 42

## Slide 109
System Interfaces
HVAC - containment (HC)
The HC system receives CIAS and SIAS signals from the ESFAS.
HVAC - fuel building (HF)
The HF system receives SIAS signals from the ESFAS.
HVAC - control building (HJ)
The HJ system receives SIAS signals from the ESFAS.
Containment hydrogen control system (HP)
The HP system receives CIAS signals from the ESFAS.
Instrument and service air system (IA)
The IA system receives CSAS signals from the ESFAS.
Nuclear cooling water system (NC)
The NC system receives CSAS signals from the ESFAS.
Non-class 1E 480V power MCC system (NH)
The NH system receives SIAS signals from the ESFAS.
Class 1E standby generation system (PE)
The PE system receives AFAS and SIAS signals from the ESFAS.
Reactor coolant (RC)
The RC system receives SIAS signals from the ESFAS.
Radioactive waste drains system (RD)
The RD system receives CIAS signals from the ESFAS.
Plant computer (RJ)
The PPS provides indication of abnormal system conditions to the RJ system.
Plant annunciator (RK)
The RK system processes pre-trip, trip, channel test, channel bypass, operation bypass and trouble signals from the PPS to alert operations personnel of the PPS status.
Balance of plant - ESFAS (BOP)
The SA system receives AFAS, CSAS and SIAS signals from the ESFAS.
Emergency response facilities data acquisition and display system (ERFDADS) (SD)
The SD system receives AFAS, CIAS, CSAS, MSIS, RAS and SIAS signal from the ESFAS.
Main steam (SG)
The SG system receives AFAS, CIAS, MSIS and SIAS signals from the ESFAS.

## Slide 110
Qualified safety parameter display system (QSPDS) (SH)
The SH system receives AFAS, CIAS, CSAS, MSIS, RAS and SIAS signals from the ESFAS.
Safety injection and shutdown cooling system (SI)
The safety injection system receives CIAS, CSAS, RAS and SIAS signals from the ESFAS.
Nuclear sampling system (SS)
The nuclear sampling system receives CIAS signals from the ESFAS.
Chilled water system (WC)
The chilled water system receives CIAS and SIAS signals from the ESFAS.
Essential lighting system (QB)
The QB system receives SIAS signals from the ESFAS.
System Interfaces

## Slide 111
Component ID | Component name | SIAS | CSAS | RAS | LOP/LS
SIA P02, SIB P02 | HPSI pump | start | start |  | stop
SIA P01, SIB P01 | LPSI pump | start | start | stop | stop
SIA P03, SIB P03 | CS pump | start | start |  | stop
659-660&664-669 | SI pump recirculation valves |  |  | close | 
615, 625, 635, 645, 616, 617, 626, 627, 636, 637, 646, 647 | SI initiation valves | open |  |  | 
671, 672 | CS iso valves |  | open |  | 
673-676 | Cont.Smp to SI vlv |  |  | open | 
322, 332 | Ht leg chk v lkg vlv | close |  |  | 
614, 624, 634, 644 | SIT outlet to loops | open (or>410psi) |  |  | 
611, 621, 631, 641 | SIT fill & drn vlvs | close |  |  | 
618, 628, 638, 648 | SI to RC loop drns | close |  |  | 
682 | Msc drn hdr RWT | close |  |  | 
On a SIAS, CSAS, RAS or LOP/LS actuation SI components respond as follows:

## Slide 112: ENGINEERED SAFETY FEATURES ACTUATION SYSTEM
Course Terminal Objective:
Given the appropriate references, the participant will be able to describe the purpose, operation, and maintenance of the Engineered Safety Features Actuation System. The participant will demonstrate mastery of the material by achieving a score of 80% or greater on a written examination at the end of the course.

## Slide 113: ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)
Enabling Objectives:
E001 IDENTIFY THE SAFETY SYSTEMS CONTROLLED BY THE AUXILIARY RELAY CABINET.
E002 DESCRIBE THE GENERAL LAYOUT AND CODING SYSTEM ASSOCIATED WITH THE AUXILIARY RELAY CABINETS.

## Slide 114
E003 DESCRIBE THE CONDITIONS NECESSARY TO INITIATE THE SAFETY SYSTEM.
E004 GIVEN A TYPICAL TRIP CIRCUIT DIAGRAM, EXPLAIN THE OPERATION OF THE CIRCUIT FOR NORMAL, TRIP, RESET AND TEST CONDITIONS.
E005 EXPLAIN SAFETY SYSTEM TRIP CIRCUITS THAT EMPLOY INTERPOSING RELAYS.
ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)

## Slide 115
E006 DESCRIBE THE OPERATION OF THE EFAS ACTUATION FROM THE CIRCUIT LOGIC TO THE ACTUATED DEVICES.
E007 GIVEN AN ESFAS TEST CIRCUIT DIAGRAM AND A FRONT PANEL DRAWING OF THE ESFAS TEST MODULE, DESCRIBE THE OPERATION OF THE TEST CIRCUITS.
E008 DESCRIBE THE SURVEILLANCE TESTS ASSOCIATED WITH ESFAS.
ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS)

## Slide 116: ENGINEERING SAFETY FEATURES ACTUATION SYSTEM (ESFAS)
EO09 Describe the use of Prevent Event Tools and Electrical Safe Work Practices to minimize human performance errors during testing or maintenance of the NSSS ESFAS.
EO10 Given examples of NSSS ESFAS maintenance problems, determine the fault using procedures, NSSS ESFAS prints, Tech Manuals, and applicable documents .

## Slide 117: END

## Slide 118
ESFAS Parameters
5-5 thru 5-7
3

## Slide 131: Look at 3.3.7
Specifically refers to DG Loss Of Voltage Start LOVS
We call it LOP

## Slide 132: Look at 3.3.8 CPIAS
One CPIAS shall be operable
During modes 1-4, core alts or fuel movement in containment
If not, shut down and close containment purge
Minimizes offsite dose in event of a fuel handling accident in containment

## Slide 133: Look at 3.3.9 CREFAS
One CREFAS shall be operable
During modes 1-6 and during fuel movement
Or place one CREFS in operation

## Slide 134: 3.7.12 CREATCS
Control Room Essential Air Temperature Control System
Actuated by CREFAS

## Slide 135
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
5-2/5-3
1

## Slide 136
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
RAS
RAS
MSIS
CSAS
CIAS
EFAS-1
SIAS
RAS
EFAS-2
STEAM GENERATOR RUPTURE CIRCUIT
LOCATED OUTSIDE CONTAINMENT

## Slide 137
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
STEAM GENERATOR RUPTURE CIRCUIT
5-2/5-3
1

## Slide 138
ESFAS ONLY (PARAMETERS 17 AND 20)
LOCATED OUTSIDE CONTAINMENT
5-2/5-3
1

## Slide 139
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
5-2/5-3
1

## Slide 140
REACTOR TRIP & ESFAS (PARAMETERS 6 THROUGH 13)
STEAM GENERATOR RUPTURE CIRCUIT
5-2/5-3
1

## Slide 141
ESFAS ONLY (PARAMETERS 17 AND 20)
LOCATED OUTSIDE CONTAINMENT
5-2/5-3
1

## Slide 145
1A
3A
4A
2A
1B
3B
2B
4B
CSAS ESFAS SIMPLIFIED LOGIC
CSAS ESFAS SIMPLIFIED LOGIC
5-5 thru 5-7
4