## Slide 1
ACADs (08-006) Covered
Keywords
BWR, main steam, piping and instrument drawing, functional operating sketch, flowpath, interrelationships, safety relief valve.
Description
Supporting Material
1.2.1.11 | 3.1.1.9 | 3.1.4 | 4.2.7.20 | 4.2.7.33 | 4.2.7.34 |  | 
Notes: <number>

## Slide 2
<number>
NUET 130 MAIN STEAM SYSTEM
The purpose of this class is to familiarize students with a BWR Main Steam system.
We will use the Functional Operating Sketch (FOS) and Piping & Instrumentation Drawing (P&ID) of the Main Steam system at Fermi 2 as the primary tools to learn this system.
Notes: <number>
<number>
<number>
<number>

## Slide 3
<number>
MAIN STEAM
TERMINAL OBJECTIVE
Students will understand the Main Steam system, its major components and flowpaths
Notes: <number>
<number>
<number>
<number>

## Slide 4
<number>
MAIN STEAM
ENABLING OBJECTIVES
State the purpose of the Main Steam system, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the Main Steam system.
Identify the modes of operation of the Main Steam system, including the major components and flowpaths associated with each mode.
Describe the basic interrelationships between the Main Steam system and other plant systems.
Notes: <number>
<number>
<number>
<number>

## Slide 5
<number>
MAIN STEAM
Purposes of the Main Steam (MS) system
To direct dry saturated steam from the Reactor vessel to:
  Main Turbine
  Reactor Feed Pump Turbines
  Moisture Separator Reheaters
  Selected Balance-of-Plant (BOP) Systems
Provides for relief of over-pressure conditions in the Reactor Pressure Vessel (RPV)
Notes: <number>
<number>
<number>
<number>

## Slide 6
<number>
MAIN STEAM
Major Flowpaths:
Four Main Steam lines (MS lines A-D) exit the RPV
Each Main Steam line contains an inboard and outboard Main Steam Isolation Valve (MSIV). The Inboard MSIVs are located in the Drywell and the Outboard MSIVs are located in the Reactor Bldg Steam Tunnel
Each Main Steam line also contains a large Motor-Operated valve called the third MSIVs, located in the Turbine Bldg. These are primarily used as maintenance isolations.
The steam lines dump into a large 52 inch diameter manifold, steam lines to each of the major loads are connected to this manifold
Each steam line also includes drain connections. The MS line drains collect into common piping and eventually dump into the Main Condenser.
Notes: <number>
<number>
<number>
<number>

## Slide 7
<number>
MAIN STEAM
DW Sump
Notes: <number>
<number>
<number>
<number>

## Slide 8
<number>
MAIN STEAM
Typical Main Steam Isolation Valve. These valves are closed automatically by various safety logic functions. Closure time is between 3-5 seconds – a function of the large springs and the upstream pressure acting on the top of the disc.
Notes: <number>
<number>
<number>
<number>

## Slide 9
<number>
MAIN STEAM
Notes: <number>
<number>
<number>
<number>

## Slide 10
<number>
MAIN STEAM
This drawing shows the pneumatic supply
and controls of the MSIVs. The accumulators
Store sufficient air/nitrogen to allow several cycles
of valve operation even if normal supply is lost.
Notes: <number>
<number>
<number>
<number>

## Slide 11
<number>
MAIN STEAM
Drawing of a typical Safety Relief Valve (SRV). These are rapid-acting valves that open at either their setpoint lift pressure, safety function logic or manual actuation from the Control Room.
Notes: <number>
<number>
<number>
<number>

## Slide 12
<number>
MAIN STEAM
Notes: <number>
<number>
<number>
<number>

## Slide 13
<number>
MAIN STEAM
Safety Relief Valves (SRVs)
15 total SRVs are mounted to the MS lines between the RPV and the Inbd MSIV.
High pressure activates the pilot valve which then causes the main valve to open. Flow through the SRV goes to quencher pipes inside the Torus below the water line. Explain why?
5 of the SRVs are part of the Automatic Depressurization System (ADS). ADS is automatically or manually initiated, causes the 5 SRVs to open, which rapidly depressurizes the reactor. More about this function in later lessons.
2 of the remaining SRVs have an additional function known as Low-Low Set. The Low-Low Set logic automatically lowers the setpoint of these 2 SRVs so that they will open and stay open in certain overpressure scenarios, preventing numerous other SRVs from having to cycle open/close.
Notes: <number>
<number>
<number>
<number>

## Slide 14
<number>
MAIN STEAM
Safety Relief Valves (SRVs)
Each SRV discharge line is equipped with a vacuum breaker to prevent water rise in pipe during cooldown and condensation after lifting.
  A vacuum drawn in the Main Steam lines can cause backflow through the SRVs which can lead to decreasing Drywell pressure. This may cause actuation of the Torus to Drywell and Rx Bldg. to Torus Vacuum Breakers.
SRVs must be tested periodically to ensure their setpoint lift pressures have not drifted and to prove that they would have been functional since their last test. Industry operating experience revealed pilot valve seat “sticking” problems many years ago. Those valve seats are now coated with platinum to avoid the sticking problem. The platinum coating is only about 20 microns thick.
Notes: <number>
<number>
<number>
<number>

## Slide 15
<number>
MAIN STEAM
Main Steam operation:
At full reactor power (100%), the steam pressure leaving the RPV is around 1030 psig. 52 Inch Manifold pressure is app. 960 psig.
Total Steam Flow 14,850,000 lbm/hr (14.85 x 106 lbm/hr)
Steam temperature 550°F
Steam Quality 99.56%
Also connected to the 52 in Manifold are the 2 MS Bypass valve lines. These lines are used to draw steam from the reactor and dump directly to the Main Condenser during turbine startup or trip conditions. This is part of the Reactor Pressure Control system, which will be covered in more detail in later lessons.
Notes: <number>
<number>
<number>
<number>

## Slide 16
<number>
MAIN STEAM
Additional Main Steam functions:
MS provides steam to the High Pressure Coolant Injection HPCI) turbine. The HPCI turbine drives a pump which then provides water to the reactor in the event of emergencies, such as Loss of Coolant Accidents (LOCA)
MS provides steam to the Reactor Core Isolation Cooling (RCIC) turbine. The RCIC turbine drives a pump which also provides water to the reactor in the event of emergencies, including LOCA
The HPCI and RCIC systems will be discussed in later sessions.
MS provides steam to the Steam Jet Air Ejectors (SJAE). The SJAEs pull a suction on the Main Condenser which helps to maintain a vacuum and also removes air and other non-condensible gasses.
Notes: <number>
<number>
<number>
<number>

## Slide 17
<number>
MAIN STEAM
Additional Main Steam functions:
Main Steam is supplied to the Reheater/ Separators to reheat (superheat) turbine steam as it passes from the High Pressure Turbine through the Reheater/Separators to the Low Pressure Turbines.
The Turbine Sealing Steam System uses Main Steam to supply sealing steam to the shaft glands of the Main Turbine and Reactor Feed Pump Turbines to prevent air leakage into the Main Condenser which could cause a loss or reduction of condenser vacuum.
Notes: <number>
<number>
<number>
<number>

## Slide 18
<number>
MAIN STEAM
Design Accident discussion:
The reactor steam output and the distance the steam has to be transported determines the allowable pressure drop and hence the total flow area required from the steam lines. One of the conditions that must be evaluated for the design of a nuclear steam plant is a hypothetical accident where one of the steam lines is assumed to break outside the primary containment. The rate at which the steam-water mixture and associated radioactivity can escape through the break depends on the cross sectional area of the broken section. The use of four steam lines permits the pipe break analysis to use a cross sectional area that is one fourth of the total steam flow area. The use of four steam lines also generates a smaller differential pressure on the reactor internals under the assumed pipe break conditions.
Notes: <number>
<number>
<number>
<number>

## Slide 19
<number>
MAIN STEAM
Review
TERMINAL OBJECTIVE
Students will understand the Main Steam system, its major components and flowpaths
Notes: <number>
<number>
<number>
<number>

## Slide 20
<number>
MAIN STEAM
Review
ENABLING OBJECTIVES
State the purpose of the Main Steam system, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the Main Steam system.
Identify the modes of operation of the Main Steam system, including the major components and flowpaths associated with each mode.
Describe the basic interrelationships between the Main Steam system and other plant systems.
Notes: <number>
<number>
<number>
<number>

## Slide 21
<number>
MAIN STEAM
QUESTIONS ??????????
Notes: <number>
<number>
<number>
<number>