## Slide 1
ACADs (08-006) Covered
Keywords
Description
Supporting Material
1.1.7.3.3 | 1.1.7.3.4 | 1.1.7.3.5 | 1.1.7.3.6 | 4.25.1.3 | 4.25.1.8
4.25.2 | 4.25.4 | 4.25.5 | 4.25.8 | 4.25.10 | 
Augusta Technical College 2011
Notes: <number>

## Slide 2: Fundamentals of Corrosion
Prepared by
Ivelisse Ortiz-Hernandez, PhD.
Source: File h1015v1 from the DOE, Module 2
<number>

## Slide 3: Objectives
Without references, DESCRIBE the causes and effects of corrosion on metals and the type of chemistry used in a plant to minimize corrosion.
<number>

## Slide 4: First Enabling Objective
1.1 DEFINE the following terms:
a. Ionization
b. Conductivity
c. Corrosion
d. Electrolysis
e. General corrosion
f. Wastage
<number>

## Slide 5: Why is corrosion control important?
Rapid localized corrosion may lead to penetration of the metal containing the coolant. Radioactive coolant would then leak from the system and jeopardize safe operation.
Corrosion of the nuclear fuel cladding may cause the cladding to become brittle and less ductile.
  The swelling from the generation of fission gases within the fuel may then cause the cladding to crack or blister, and highly radioactive fission products may then be released to the coolant.
Some of the metallic oxide corrosion products released to the coolant may be deposited on surfaces in the reactor core.
  The solids when in contact with the neutron flux become radioactive and accumulate in different regions throughout the system and outside the core.
  Results in issues with maintenance and radiation levels outside the core.
<number>

## Slide 6: Basic Definitions
Current is the flow of electrons through a medium. A metal conducts electricity without changing its properties. This is called metallic conduction.
Ionization is the process of adding electrons to or removing electrons from atoms or molecules, creating ions. High temperatures, electrical discharges, and nuclear radiation can cause ionization.
  Current can be conducted by the movement of these ions.
The compounds that conduct electric current by ion movement are called electrolytes, and this ionic motion is call electrolytic conduction.
Conductivity is a measure of the ability of a substance to allow electron flow.
  Conductivity indicates the amount of ions in solution, which relates directly to the potential of corrosion taking place.
<number>

## Slide 7: Definition of Corrosion
Corrosion is the deterioration of a material due to interaction with its environment.
Electrolysis is the decomposition by electric current (in the context of corrosion the use of electrical current to bring about chemical change).
An electrolyte is defined as an electricity-conducting fluid; that is, it has positive and negative ions that can move and constitute an electrical current.
Pure water is a poor conductor (contains H+ and OH- ions only). When a salt is added it becomes a good conductor.
Corrosion is electrochemical in nature because the corrosive chemical reactions involve transfer of charge.
<number>

## Slide 8: Corrosion of Iron in the presence of water or acidic water
Iron goes into solution as Fe++ ions. As these ions go into solution, the metal becomes negatively charged (by the electrons left behind) with respect to the electrolyte.
Potential difference is observed.
<number>

## Slide 9: Electrochemical Cells
The sites at which the oxidation takes place on the surface of the metal become electrochemical cells made up of micro-electrodes of the two different substances; the metal and the electrolyte.
These micro-electrodes set up many micro-cells connected through the bulk of the metal.
The ability of a metal to corrode will depend on the potential difference between the metal and the electrolyte.
  For example, magnesium and zinc go into solution to a greater extent than iron, and these metals will be more negative with respect to the electrolyte than iron.
  Nickel, lead, and copper go into solution less readily and produce a smaller potential difference.
  The potential difference depends on the ability of the metal to gain or loose electrons.
Table 1 lists the potential differences for various metals in water. It changes with different electrolytes.
<number>

## Slide 10
<number>
Notes: Reference electrode is a hydrogen electrode
<number>

## Slide 11: Two Types of Electrochemical Cells
<number>

## Slide 12: Electrochemical Cells
Oxidation potential describes the ability to loose electrons. This takes place at the anode.
Reduction potential reflects the ability to gain electrons. Takes place in the cathode.
The potential is measured with respect to a reference. In this case, the reference is the hydrogen electrode.
The most negative potentials represent the strongest reducing agents.
Types of cells: galvanic (electrodes of two different substances) and concentration cells (same electrodes with different concentrations).
<number>

## Slide 13: Electrochemical Cells
<number>
There are two types of electrochemical cells: galvanic (ones that spontaneously produce electrical energy) and electrolytic (ones that consume electrical energy).

## Slide 14
<number>
A potential difference between two electrodes represents a tendency for the reaction to occur.

## Slide 15
For electrochemical reactions to take place the microcells must be interconnected.
Connection established by the water/electrolyte solution and the cells produce electrical current allowing the reaction to take place.
Normally the reaction is expected to continue until the difference in potential between the negatively charged metal and positively charged solution is zero.
  In this case iron will not leave the surface.
  Impurities and imperfections will cause preferential oxidation of one region versus another resulting in localized corrosion.
<number>

## Slide 16: Oxidation and Reduction Reactions
The corrosion of a metal (that is, the chemical transformation that is recognized as destructive to the metal) is the oxidation step of the overall oxidation-reduction process.
Oxidation is the process of losing electrons; reduction is the process of gaining electrons.
<number>
Example of a REDOX reaction
Notes: <number>

## Slide 17: Oxidation and Reduction Reactions
After the metal looses electrons it forms a positively charged ion.
The reaction takes place at the anode.
The cations (positive ions) may then go into solution, or they may combine with any available anions (negative ions) or water to form ionic compounds.
The metal decomposes as it corrodes.
Oxidation must be followed by a reduction.
For most metals in an aqueous environment, the important reduction half-reaction is the reduction of hydronium ions (a hydronium ion is simply a hydrogen ion attached to a water molecule).
<number>

## Slide 18: Corrosion Types
The corrosion in a plant depends in the minerals present in the cooling water and the dissolved oxygen.
During corrosion a chemical reaction takes place at the water-metal interface.
General corrosion – widespread chemical reaction in the metal surface.
Localized corrosion – occurs when specific areas are attacked faster than others.
  Affected by different conditions in a localized area like stress, fatigue, erosion, and other forms of chemical attacks.
<number>

## Slide 19: General Corrosion
Results in the uniform removal of material from all metal surfaces in contact with water.
Corrosion takes place in the surface of one metal.
Corrosion is dependent on the composition of the water, the type of metal, and the environmental conditions in the plant.
Iron is unstable when in contact with water and dissolves to form ferrous ion (Iron (II) ion) while releasing electrons.
<number>

## Slide 20: Wastage
Corrosion specifically refers to any process involving the deterioration or degradation of metal components.
Corrosion processes are usually electrochemical in nature, having the essential features of a battery.
  When metal atoms are exposed to an environment containing water molecules they can give up electrons, becoming themselves positively charged ions, provided an electrical circuit can be completed.
This effect can be concentrated locally to form a pit or, sometimes, a crack, or it can extend across a wide area to produce general wastage.
Notes: Corrosion Theory
http://events.nace.org/library/corrosion/Principles/Theory.asp
Corrosion Control in Engineering Design
http://www.npl.co.uk/upload/pdf/corrosion_control_in_engineering_design.pdf
<number>

## Slide 21: Wastage
Wastage Corrosion Tests
Saturated Boric Acid Solution at 97.5°C
Molten H–B–O Environment at Ambient Pressure
High–Temperature High–Pressure Boric Acid Solutions
Effect of Chromium Content on Corrosion Rate
Notes: Boric Acid Corrosion of Light Water Reactor Pressure Vessel Materials
http://www.nrc.gov/reading-rm/doc-collections/nuregs/contract/cr6875/into-acknowledgments.pdf
<number>

## Slide 22: General Corrosion
When the ferrous ions come into contact with hot water the reduction of hydrogen takes place.
The iron (II) ion reacts to form mangnetite (Fe3O4).
The magnetite forms a protective layer.
<number>

## Slide 23: General Corrosion
As the reaction takes place, the ferrous ions must pass through this layer to further react with water.
Once a thick enough layer is formed, the reaction slows down considerably.
Problem: If the magnetite particles are released into the stream of water, the particles can cause problems in small passages.
New systems go through a “conditioning” process to intentionally form a stable corrosion layer.
<number>

## Slide 24: Corrosion Mechanism: Formation of Rust
<number>

## Slide 25: Passivity and Polarization of a Metal
Metals that normally fall victim to corrosion will sometimes exhibit a passivity to corrosion.
Passivity is the characteristic of a metal exhibited when that metal does not become active in the corrosion reaction.
Passivity is caused by the buildup of a stable, tenacious layer of metal oxide on the surface of the metal.
Once the layer, or film, is formed, it acts as a barrier separating the metal surface from the environment.
The steel example above discusses the use of passivity in a process.
<number>

## Slide 26
Metals such as zirconium, chromium, aluminum, and the stainless steels form thin, tenacious oxide films when exposed to the atmosphere or to pure water at room temperature.
  Very effective in minimizing further corrosion.
<number>

## Slide 27
An active electrochemical cell (oxidation-reduction reaction) is an unstable chemical system.
The potential associated with a galvanic cell, for example, steadily decreases as current flows and the oxidation-reduction reaction proceeds. Reaction stops when the electric potential goes to zero (no net reaction).
  At this point the system is at equilibrium.
In electrochemical cells, the decrease in cell potential caused by the operation of the cell (current flow) is called polarization.
<number>
Notes: Depolarized versus polarized. Search for polarization in terms of corrosion versus polarization with respect to electrical circuits.
An increased resistance to the flow of current in a voltaic cell, caused by chemical reactions at the electrodes. Polarization results in a reduction of the electric potential across the voltaic cell.
<number>

## Slide 28
An active electrochemical cell (oxidation-reduction reaction) is an unstable chemical system.
The potential associated with a galvanic cell, for example, steadily decreases as current flows and the oxidation-reduction reaction proceeds. Reaction stops when the electric potential goes to zero (no net reaction).
  At this point the system is at equilibrium.
In electrochemical cells, the decrease in cell potential caused by the operation of the cell (current flow) is called polarization.
<number>
Notes: Depolarized versus polarized. Search for polarization in terms of corrosion versus polarization with respect to electrical circuits.
An increased resistance to the flow of current in a voltaic cell, caused by chemical reactions at the electrodes. Polarization results in a reduction of the electric potential across the voltaic cell.
<number>

## Slide 29: Example of Corrosion
For example, for galvanic corrosion to take place we need two dissimilar metals with a difference in their potential.
As the reaction takes place, Zn+2 ions (produced by the oxidation of zinc metal) pass into solution. The Cu+2 ions in solution are reduced as the copper metal plates out.
Thus, the concentration of Zn+2 in solution increases and the concentration of Cu+2 decreases according to the following overall reaction.
<number>

## Slide 30: Galvanic Cell
<number>
As Zn+2 increases and Cu+2 decreases, the electrical potential decreases.
This decrease in cell potential, which results from changes in concentrations, is one form of polarization called concentration polarization.
Notes: <number>

## Slide 31
Polarization is the decrease in cell potential caused by the operation of the electrochemical cell.
Polarization can be in two forms; concentration or activation.
  Concentration polarization is associated with the concentration of ions in solution which shields the metal, thereby causing a decrease in the electrical potential of the cell.
  Activation polarization is the formation of a layer containing absorbed hydrogen atoms that block the metal's surface from the corrosion process.
<number>

## Slide 32: Galvanic Cell: Zinc and Platinum Electrode
<number>
Again, as the cell operates, the cell
potential drops.
The decrease is partially due to the increase in Zn+2 concentration and the decrease in H3O+ concentration.
The second type of polarization is associated with the reduction half-reaction.
Hydrogen ion remains in the surface of the Pt electrode until it either recombines with a second hydrogen atom to form molecular hydrogen, H2 or are removed by reacting with oxygen to form water.
The sites are blocked until the hydrogen is removed.

## Slide 33: Galvanic Cell: Zinc and Platinum Electrode
Reaction 2.6 is the slowest step in the process because it requires the greatest amount of energy to proceed (highest activation energy).
  2H  H2 Reaction 2.6
Because the oxidation half-reaction can occur no faster than the reduction half-reaction, the rate of the overall oxidation-reduction reaction is controlled by the reaction of Equation (2-6).
This type of polarization is called activation polarization and is sometimes referred to as hydrogen polarization, or cathodic polarization, because the polarizing reaction occurs at the cathode.
Both concentration and activation polarization decrease the net oxidation-reduction reaction rate.
In corrosion processes, activation polarization usually has the greater effect.
<number>

## Slide 34: General Corrosion
Conditions that lead to general corrosion
  1) metal and water in the same environment, and
  2) a chemical reaction between the metal and water that forms an oxide.
<number>

## Slide 35: Oxidation of Iron
Under operating conditions, assume that the water is deaerated, at room temperature and with a pH close to neutral.
<number>

## Slide 36
Once the oxide layer has formed the metal is not in direct contact with the water. For the reaction to continue the electrons and ions most diffuse through this layer.
The magnetite layer develops in between the Ferrous oxide and ferric oxide layer.
The electrons participate in the reduction reaction with hydronium ions.
These latter reactions are believed to take place predominately at the oxide-water interface, but some reaction may occur within the oxide layer by the diffusion of H+ , OH- , and H2O into the layer.
<number>

## Slide 37
<number>
The protection provided by the film depends on the tenacity of the film.
A loosely attached film will continue to corrode. If defects develop in the film, corrosion will take place.

## Slide 38: Factors Affecting General Corrosion Rate
Corrosion rates increase as temperature increases.
Temperature and pressure of the medium govern the solubilities of the corrosive species in the fluid, such as oxygen (O2 ), carbon dioxide (CO2 ), chlorides, and hydroxides.
A rule of thumb is that the reaction rate doubles with a 20°F to 50°F temperature rise. This linear increase with temperature does not continue indefinitely due, in part, to a change in the oxide film.
High fluid velocities can remove the corrosion layer and increase the rate of corrosion.
  Known as erosion.
  Water velocities of 30 to 40 ft per second are usually considered to cause erosion.
<number>

## Slide 39
The presence of oxygen in water increases the corrosion rate.
The reason for this increase is the rapid reaction between oxygen and the polarizing layer of atomic hydrogen absorbed on the oxide layer.
Reaction 2.11 removes the polarizing layer.
Overall reaction:
<number>
Notes: <number>

## Slide 40
Oxygen, therefore, has two effects:
  it removes the polarizing layer of atomic hydrogen, and
  it can react directly with the metal or metal oxide; thus, the corrosion rate increases.
Oxygen is known as a depolarizer.
pH also affects the corrosion rate.
At a pH of less than 4 the FeO is soluble.
In the range of pH 4 to pH 10, the corrosion rate of iron is relatively independent of the pH of the solution.
<number>
Notes: <number>

## Slide 41
At lower pH the film cannot accumulate in the surface of the metal.
  Corrosion takes place at a higher rate.
At pH above 10 corrosion rate decreases.
This is believed to be due to an increase in the rate of the reaction of oxygen with Fe(OH)2 (hydrated FeO) in the oxide layer to form the more protective Fe2O3 (note that this effect is not observed in deaerated water at high temperatures).
<number>

## Slide 42: Effect of pH
In the range of pH 4 to pH 10, the corrosion rate of iron is relatively independent of the pH of the solution.
For pH values below 4.0, ferrous oxide (FeO) is soluble. Thus, the oxide dissolves as it is formed rather than depositing on the metal surface to form a film. Formation of hydrogen at lower pH means that depolarization with oxygen and hydrogen evolution are both playing a role.
<number>

## Slide 43
<number>
Corrosion layer is compromised at low and high pH at higher temperatures.
A pH between 7 and 10 gives a lower rate of corrosion.
The pH is always maintained alkaline to minimize corrosion rate.
Having hydrogen in the water helps minimize the amount of corrosion by eliminating the amount of oxygen in the system.
Dissolved oxygen reacts with the protective hydrogen gas layer at the cathode to form water.

## Slide 44: Aspects Affecting Corrosion Rate
The condition and composition of the metal surfaces affects the corrosion rate.
  Deposits, scale, or irregular surfaces create areas on the metal where local corrosion can initiate and proceed at a faster rate than normal.
When iron or steel is exposed to high temperature water, the rate of corrosion of the metal is observed to decrease with exposure time during the early period of exposure.
  After exposure to hot water for a few thousand hours the corrosion rates reaches equilibrium at a low level of corrosion.
  The rate at which the corrosion layer develops decreases as the level of corrosion slows down. After a few thousand hours, the film does not grow any longer.
<number>

## Slide 45
Because a tightly adhering corrosion film inhibits further corrosion, great care is taken during the initial fill of reactor plants to promote formation of the best possible corrosion film.
This process, referred to as pretreatment, or pickling, involves careful control of reactor coolant water chemistry and temperature during the pretreatment period.
<number>
Notes: <number>

## Slide 46: Prevention Chemistry Control
Plant chemistry is used to prevent corrosion.
Things done to minimize corrosion include:
  Passivators and inhibitors
    Passivation is the condition where a naturally active metal corrodes at a very low rate, probably due to an oxide coating or an absorbed layer of oxygen.
    Some chemical substances, called passivators or inhibitors, if added to water, can provide this type of passivation by undergoing reduction at the metal surface. Example: Potassium Chromate.
  Cathodic Protection
    The use of cathodic protection, supplying an external electric current to the iron so that it acts as a cathode and has no anodic areas, is another method of preventative chemical control. Uses a sacrificial electrode as an anode: Zinc.
<number>

## Slide 47: Prevention Chemistry Control
Removing Corrosive agents
  One method is using deaerators to remove dissolved oxygen and to a lesser extent carbon dioxide.
  Treating the water by softening and demineralization removes the dissolved solids and reduces the conductivity.
Chemical Addition
  Involves the addition of a chemical that will alter a chemical reaction or tie up a common corrodant.
  Filming amines (organic compounds that are derivatives of ammonia) accomplish protection by forming adhering organic films on metal surfaces to prevent contact between corrosive species in the condensate and the metal surface.
  Phosphates and sodium hydroxide are used to adjust the system pH and remove hardness.
<number>

## Slide 48: Corrosion of Aluminum
Variables include environment, temperature, alloy in question, flow velocities, impurities present in the environment, and chemistry conditions to which it is exposed.
An additional factor that affects corrosion is pretreatment.
Pretreatment, soluble and solid impurities, and chemistry are within the control of the operator and will be discussed in this text.
Experiments have shown that prefilming limits corrosion on aluminum-clad fuel assemblies.
Impurities are major contributors to the corrosion of aluminum.
  Sources include the Make up water and impurities from corrosion in other parts of the process. Organic impurities due to resin residues from the ion exchangers can also be observed.
<number>

## Slide 49: Corrosion of Aluminum
Chemistry controls, including pH, dissolved oxygen, and conductivity, greatly influence the formation and propagation of the oxide film on aluminum surfaces.
Conductivity is a quantitative indication of the impurities present in the system, and pH theoretically dictates the value of conductivity.
Extensive tests carried out in support of DOE test reactors have revealed that minimum aluminum corrosion results with a pH of 5.0 at normal operating temperatures.
Additionally, studies have shown that the aluminum corrosion products also exhibit a minimum solubility at a pH near 5.5 at 25ºC.
It should be noted that the values at which minimum corrosion and solubility are found shift to a lower pH as the temperature is increased. For example, at 300ºC, the value for minimum aluminum corrosion is near pH 3.0.
<number>

## Slide 50
<number>

## Slide 51: Corrosion of Aluminum
The conditions that have proven to be most effective in limiting corrosion of aluminum are as follows.
  Maintaining pH slightly acidic with the value of the pH depending largely upon operating temperature
  Elimination of dissolved oxygen
  Elimination of soluble and solid impurities
  Prevention of the introduction of organic impurities
  Pretreatment (or pickling)
  Maintaining water purity
<number>

## Slide 52: Crud
In addition to the corrosion film, corrosion products in the form of finely divided, insoluble oxide particles called crud become suspended in the reactor coolant or loosely adhere to metal surfaces.
It can accumulate and foul heat-transfer surfaces or clog flow passages.
It becomes activated when exposed to radiation.
Because crud can be transported throughout the reactor coolant system, it can collect outside the reactor core, causing radiation hot spots that increase ambient radiation levels.
Hot spots caused by collections of crud may occur at the entrance to the purification heat exchanger and other areas of low flow velocity.
<number>

## Slide 53
The crud release can result from an increased oxygen concentration, a reduced (or significantly changed) pH, a large temperature change (heatup or cooldown), or a physical shock to the system.
Physical shocks include starting, stopping, or changing pump speeds, or other evolutions like a reactor scram or a relief valve lift.
A sudden release of crud is called a crud burst.
  Crud bursts often lead to the removal of protective corrosion films and make the freshly exposed metal more susceptible to additional corrosion.
Another corrosion byproduct is scale, which is made up of deposits on surfaces from the formation of insoluble compounds from normally soluble salts.
  Most common are calcium or magnesium carbonates (CaCO3 or MgCO3 ).
<number>

## Slide 54: Alloys used in a Nuclear System
<number>

## Slide 55: Stainless Steel
Composed of Iron, Chromium and Nickel. Also contains carbon.
The addition of at least 12% chromium is what makes it resist corrosion.
The iron, chromium and nickel still undergo corrosion.
  Form: Nickel oxide (NiO), Chromium oxide (Cr2O3), and magnetite (Fe3O4)
  Black layer that adheres strongly to the surface of the metal.
<number>

## Slide 56: Zirconium Alloys
Its surface reacts in a similar way under the presence of water. It reacts to form ZrO2.
Zirconium does not absorb protons through it.
It has a high melting point, adequate strength up to 800ºF, and low neutron absorption.
The oxide layer prevents further corrosion from taking place.
Zircaloys are normally used in the core of the reactor.
The corrosion layer formed in this alloy is a passivation layer.
<number>

## Slide 57: Composition of Zircaloy
More than 95% Zirconium and less than 2% of tin, niobium, iron, chromium, nickel and other metals.
Corrosion of Zircaloy must be avoided because it leads to the formation of hydrogen which diffuses through the structure of the metal.
Hydrogen reacts with zirconium to form zirconium hydride.
  Zirconium hydride is not as strong as the alloy itself.
  Results in a weakened cladding.
<number>

## Slide 58: Zirconium Alloys
Hydrogen embrittlement can take place.
  The hydrogen can diffuse into the metal structure and react to form zirconium hydride.
  Zirconium hydride is brittle, which can weaken the metal and cause structural failure.
  Hydrogen is often a by-product of corrosion.
  It is very important to understand that this alloy is a barrier to the release of fission products (cladding).
<number>

## Slide 59: Zirconium Alloys
Zircaloy-4 is less susceptible to hydrogen embrittlement than zircaloy-2 because: Zircaloy-4 contains less nickel.
The introduction of niobium into zircaloy-4 reduces the amount of hydrogen absorption in the metal.
Cladding-protective or insulating layer added on top of another metal.
Used to isolate radiation from escaping the system.
<number>

## Slide 60: Inconel
Composed mainly of nickel (76%)
Also contains chromium.
It forms a corrosion layer that contains NiO and chromium oxide.
The corrosion layer serves as a barrier and minimizes further corrosion.
Very slow corrosion rate.
Used in the reactor core and other critical components.
Has a very high temperature resistance and is used for extreme conditions.
Forms a thick self-passivating corrosion layer.
<number>
Notes: Where is the Inconel used in the reactor core? Is it used as the metal where the zircaloy is attached to?
<number>

## Slide 61: Environmental Effects on Corrosion
Variables include
  Temperature
  Flow rate (velocity of the fluid)
  Chemical composition of the solution
  Radiation
<number>

## Slide 62: Temperature
As temperature increases corrosion rate increases.
  Heat transfer surfaces (heat exchangers) are greatly affected.
  Corrosion makes it harder to transfer heat through the metal (lower thermal conductivity).
  The thicker the corrosion layer, the greater the amount of heat needed to maintain a constant operating temperature in the reactor core.
  As the temperature is increased, then the corrosion rate also increases.
<number>

## Slide 63: Velocity
At high velocity, the corrosion layer will be relatively thin.
  The film in contact with the metal is mechanically scrubbed by the passing fluid.
Low flow rate areas have a higher corrosion rate.
  Corrosion products can settle on this areas.
  Causes maintenance problems because of possible radiation “hotspots”.
  Additional protection measures must be taken if repairs must be made in an area affected by high radiation levels (reactor drain).
<number>

## Slide 64: Chemicals in the Water
Chloride ions attack steel, fluoride attacks zirconium, and zinc causes damage to inconel.
Heavy metals (lead, mercury) cause damage in Nickel containing metals (inconel and stainless steel).
The presence of these contaminants must be avoided.
<number>

## Slide 65: Environmental Concern: Radiation
High levels of radiation can change the structure of a metal oxide layer.
The corrosion products can become activated when they are exposed to the core.
Loose particles become a radiation hazard (precipitates on radioactive surfaces)
<number>

## Slide 66: Things to avoid
Thermal shocks
  Sudden temperature changes.
Chemical shocks
  Bad Chemistry
Mechanical shocks
  Possible from pump starts
<number>

## Slide 67: Control of General Corrosion
Reduce Oxygen Content
Use corrosion inhibitors
Maintain a neutral to basic pH
<number>

## Slide 68: Control of General Corrosion
Reduce Oxygen Content
  Use deaerated water
  Maintain excess hydrogen in the water (to react with any oxygen)
  Adding an oxygen scavenger (like Hydrazine, N2H4) (Only at low temperatures).
<number>

## Slide 69: Localized Corrosion
<number>
Localized corrosion takes place a lot faster than general corrosion.
In extreme cases, failure with localized corrosion will take just days.
Only specific metals under specific conditions are susceptible to localized corrosion.

## Slide 70: What is stress?
<number>
When a metal is subjected to a load (force), it is distorted or deformed, no matter how strong the metal or light the load.
  Elastic strain – regains its shape
  Plastic strain – if after the load is applied the shape is not regained.
The phenomenon of elastic strain and plastic deformation in a material are called elasticity and plasticity, respectively.
Atoms in a material are arranged in a specific geometry which depends in the intermolecular interactions.
To distort the pattern of a crystal, work most be done in the material.
Work = Force times the distance that the force moves
Stress is the internal resistance, or counterforce, of a material to the distorting effects of an external force or load.

## Slide 71: Example of a Crystal Lattice Structure
<number>

## Slide 72: Types of stress
<number>
  Residual stresses are due to the manufacturing processes that leave stresses in a material. Welding leaves residual stresses in the metals welded.
  Structural stresses are stresses produced in structural members because of the weights they support.
  Pressure stresses are stresses induced in vessels containing pressurized materials.
  Flow stresses occur when a mass of flowing fluid induces a dynamic pressure on a conduit wall. The force of the fluid striking the wall acts as the load.
  Thermal stresses exist whenever temperature gradients are present in a material. Different temperatures produce different expansions and subject materials to internal stress.
  Fatigue stresses are due to cyclic application of a stress. The stresses could be due to vibration or thermal cycling.

## Slide 73: Types of stress
<number>
Tensile stress is that type of stress in which the two sections of material on either side of a stress plane tend to pull apart or elongate.
Compressive stress is the reverse of tensile stress.
Shear stress exists when two parts of a material tend to slide across each other in any typical plane of shear upon application of force parallel to that plane.
Compressibility is the ability of a material to react to compressive stress or pressure.

## Slide 74: Types of Localized Corrosion
<number>
Stress Cracking Corrosion
Caustic Corrosion
Galvanic Corrosion
Crevice Corrosion
Pitting Corrosion

## Slide 75: Localized Corrosion
<number>
Stress Cracking Corrosion
  Occurs in all alloys
  Stress corrosion cracking (SCC) is a type of intergranular attack corrosion that occurs at the grain boundaries under tensile stress.
  Most pure metals are immune to this type of attack.
  According to the most widely accepted theory, stress corrosion cracking is caused by a process called chemisorption. Unlike relatively weak physical absorption, such as hydrogen gas on platinum metal, chemisorption may be thought of as the formation of a compound between the metal atoms on the surface as a monomolecular layer of the chemisorbed substance, such as Cl-, OH-, Br-, and some other ions.
  Conditions for this corrosion to exist
    Susceptible metal alloy and a corroding substance
    Tensile stress
    Oxygen in water
    Temperature greater than 140 ºF
  A large tensile stress is required for it to occur.

## Slide 76: Localized Corrosion
<number>
Stress Cracking Corrosion, cont.
  The stress can come from service loads, residual stress from manufacturing processes, mismatch of components during construction, or a wedging action due to accumulation of corrosion products.
  Once a stress is present, the other factors must also be present for corrosion to occur.
  A defect initially present then grows as the metal atoms separate under stress, more chemisorption occurs, and the process continues.
  Stainless steels containing 18 percent chromium and 8 percent nickel are susceptible to cracking in environments containing chloride ions and in concentrated caustic environments (that is, in environments where the hydroxyl ion concentration is high).
  If the environment is severe enough, cracking can occur in a very short period of time.

## Slide 77: Localized Corrosion
<number>
Stress Cracking Corrosion, cont.
  To minimize:
    Careful fabrication of plant components
    Maintain chloride, fluoride and oxygen content below the specified limits.
    If oxygen is kept at very low limits, then higher chloride and fluoride limits can be tolerated.
    The reverse is also true.

## Slide 78: Chloride Stress Cracking Corrosion
The three conditions that must be present for chloride stress corrosion to occur are as follows.
  Chloride ions are present in the environment
  Dissolved oxygen is present in the environment
  Metal is under tensile stress
Chloride stress corrosion involves selective attack of the metal along grain boundaries.
In the formation of the steel, a chromium-rich carbide precipitates at the grain boundaries leaving these areas low in protective chromium, and thereby, susceptible to attack.
This form of corrosion is controlled by maintaining low chloride ion and oxygen content in the environment and the use of low carbon steels.
<number>
Notes: <number>

## Slide 79: Chloride Stress Cracking Corrosion
Chloride ions can enter these systems via leaks in condensers or at other locations where auxiliary systems associated with the nuclear facility are cooled by unpurified cooling water.
<number>

## Slide 80: Chloride Stress Cracking Corrosion
Chloride stress corrosion is a particularly significant problem in the operation of nuclear facilities because of the wide use of austenitic stainless steel, and the inherent presence of high tensile stresses associated with pressurization.
Chloride stress corrosion cracks have been known to propagate in austenitic stainless steel at stresses of about one-fifth yield strength with chloride concentrations of less than 50 ppm.
<number>

## Slide 81: Chloride Stress Cracking Corrosion
<number>

## Slide 82: Localized Corrosion
<number>
Caustic Corrosion
  Occurs in zircalloy and ferrous metal (iron containing metals).
  Conditions required
    Susceptible metal
    Concentrated Caustic conditions (pH close to 14)
    Tensile stress
  Difference between tensile stress corrosion and caustic corrosion is the chemicals involved to start the reaction.

## Slide 83: CR1.1 Corrosion rate as a function of pH
<number>

## Slide 84: CR1.1 Corrosion rate as a function of pH
<number>
Under very caustic conditions, corrosion rate increases (pH = 14)
pH should be maintained between 7 and 10

## Slide 85: Localized Corrosion
<number>
Caustic Corrosion
  To minimize general corrosion of most metal a pH of 7 or greater.
  pH = 11.3 – zircaloy corrosion layer is dissolved (pH must be maintained below 11.3 to ensure that the zircaloy layer is protected)
    Exposure of the zircaloy structure increases the chances of zirc-hydriding.
  The concentrated basic conditions are caused by boiling (basic solution concentrates in crevices). The caustic material plates out of solution. When it is remoistened it creates a region with a highly caustic environment.
  Improved resistance to caustic stress corrosion cracking can be given to Inconel by heat treating it at 620ºC to 705ºC, depending upon prior solution treating temperature.
  Strict pH control is the only solution.
    Materials cannot be changed and boiling cannot be avoided.

## Slide 86
<number>
Corrosion for Inconel
Following the grain boundaries
Corrosion for 316 stainless steel

## Slide 87: Galvanic Corrosion
<number>
Two dissimilar metals in contact of electrically conductive water.
  One of the metals can develop accelerated corrosion.
  The metals must have a different electric potential for the reaction to occur.
  The difference in potential creates a small current (flow of electrons).
  The metal with the lower oxidation potential readily oxidizes in water.

## Slide 88: Galvanic Corrosion
<number>
Required Conditions
  Two dissimilar metals in contact
  Oxygen dissolved in water
Both Cu and Zn are oxidized in the presence of oxygen in water.
The electric potential of copper is 1.90 and for zinc is 1.65.
Electrons flow from least potential to higher potential.
Copper does not corrode and zinc corrodes at an accelerated pace.

## Slide 89: How can we do to minimize corrosion?
<number>
Reactions
To minimize it
  Use corrosion resistant materials
  Use materials with similar electronegativity. For example: Cupper and Nickel: 1.90 and 1.91.
  Use sacrificial anode (to corrode this material intentionally)
  Use a transition piece between the metals (the transition piece must have similar properties than the two metals.
Prevented by minimizing the oxygen content in water.

## Slide 90: Crevice Corrosion
<number>
Is a type of galvanic corrosion.
Involves two pieces of the same metal.
Conditions for it to occur
  Two closely fitted parts
  Soluble salts or oxygen in water.
  Occurs if a difference in oxygen concentration or salt concentration exist between the crevice and the surface.
  The increase concentration of salt in the crevice increases the corrosion in this area.

## Slide 91: Crevice Corrosion
<number>
http://www.corrosion-doctors.org/Forms-crevice/
Notes: <number>

## Slide 92: Crevice Corrosion
<number>
In stage three of the crevice development a few more accelerating factors fully develop:
  The metal ions produced by the anodic corrosion reaction readily hydrolyze giving off protons (acid) and forming corrosion products. The pH in a crevice can reach very acidic values, sometimes equivalent to pure acids.
  The acidification of the local environment can produce a serious increase in the corrosion rate of most metals. See, for example, how the corrosion of steel is affected as a function of water pH.
  The corrosion products seal even further the crevice environment.
  The accumulation of positive charge in the crevice becomes a strong attractor to negative ions in the environment, such as chlorides and sulfates, that can be corrosive in their own right.
From: http://www.corrosion-doctors.org/Forms-crevice/crevice3.htm

## Slide 93: Crevice Corrosion
<number>
To minimize
  Keep water very pure.
  Soluble salt and oxygen must be minimized.
  Larger crevices (to minimize high concentration areas)
  Continuous movement of the parts will minimize it.

## Slide 94
Pitting corrosion occurs where the anodic site becomes fixed in a small area and the formation of holes (deep attack) in an otherwise unaffected area takes place.
Crevice corrosion is a type of pitting corrosion that occurs specifically within the low flow region of a crevice.
<number>

## Slide 95
<number>
Air (or oxygen) is bubbled around one electrode, and nitrogen is bubbled around the other. A current flows through the wire connecting the two electrodes.
The difference in potential is a result of the difference in oxygen concentration at the two electrode surfaces.
At the electrode exposed to nitrogen, electrons are given up by the iron as it is oxidized.
As a result, oxidation occurs at the electrode exposed to nitrogen and reduction occurs at the aerated electrode. Corrosion takes place in the oxygen free area and reduction takes place in the cathode.

## Slide 96
Oxidation occurs at the electrode exposed to nitrogen and reduction occurs at the aerated electrode.
Oxidation at one electrode and reduction at the other creates a potential and a flow of current through the connecting wire.
Note that loss of metal occurs at the electrode that is deficient in oxygen.
In iron that is exposed to water, a similar action can occur if adjacent areas of the metal surface become exposed to solutions with different oxygen concentrations.
Oxygen in the solution inside the crevice will be depleted initially by the corrosion reaction.
<number>

## Slide 97
A differential in the oxygen concentration inside the crevice versus outside the crevice results in a concentration cell.
The two adjacent areas then establish a concentration cell with electrons flowing from the region of low oxygen concentration to the region of high concentration.
Thus, metal goes into solution (oxidation) inside the crevice, and reduction occurs outside the crevice.
Metal ions diffuse out of the crevice, more metal dissolves, and the process continues. This results in the formation of a pit inside the crevice.
<number>

## Slide 98
<number>

## Slide 99
The presence of oxygen can also promote pitting at areas on the metal surface that are initially anodic with respect to an adjacent area.
For example, suppose that adjacent areas on a metal surface exhibit slightly different oxidation potentials.
Oxidation, or loss of metal, proceeds at the region of higher potential.
The overall result is corrosion, or wasting away, of the metal in the anodic region under the thicker film.
Thus, a pit in the metal surface is formed under the mound of surface oxide, as illustrated in Figure 13.
Pitting of this type is common in both low temperature and high temperature iron-water systems if precautions are not taken to remove the oxygen from the water within the system.
<number>

## Slide 100
<number>

## Slide 101
Pitting and crevice corrosion are a major hazard to a nuclear facility because of the rapid penetration of the metal with little overall loss of mass.
A nuclear facility minimizes pitting and crevice corrosion by the following actions.
  Avoiding stagnant or low flow conditions.
  Using metals and alloys that are less susceptible to the corrosion.
  Avoiding agents in the medium that cause pitting (for example, chlorides and oxygen).
  Designing the system and components such that no crevices are present.
<number>

## Slide 102: Pitting Corrosion
<number>
Caused by inconsistencies in material composition of the metal and the presence of oxygen and fluoride or chloride.
When the material has differences in potential in nearby portions corrosion can occur.
Oxygen attacks the area most prone to corrosion. The presence of chlorides accelerate the corrosion rate.
Corrosion forms a pit that can eventually cause a rupture.
Minimize by using homogeneous metals and minimizing the presence of oxygen and chloride in solution.

## Slide 103: Control of localized corrosion
<number>
Low chloride concentration
Low fluoride concentration
Low oxygen concentration
Neutral to moderate basic pH
Avoid heavy metals like mercury

## Slide 104: Reference
<number>
http://www.hss.energy.gov/nuclearsafety/ns/techstds/standard/hdbk1017/h1017v1.pdf
http://www.corrosion-doctors.org/Forms-SCC/scc.htm