## Slide 1
ACADs (08-006) Covered
Keywords
Visual, surface, volumetric, specification, procedure, standard, regulation, code discontinuity, defect, relevant condition, evaluation, micrometer, caliper, depth gauge, thread pitch gauge, feeler gauge, weld gauge.
Description
Supporting Material
5.1.2.13.4 | 5.1.2.13.6 |  |  |  |  |  | 
Notes: <number>

## Slide 2
NE 110 – Introduction to NDT & QA/QC
Visual Inspection
Prepared by:
Chattanooga State Community College
Notes: <number>

## Slide 3: Types of Examinations
Per Section XI of the ASME Boiler and
Pressure Vessel Code (Rules for Inservice
Inspection of Nuclear Power Plant
Components), there are three types of
examinations used during an inservice
inspection:
      Visual
      Surface
      Volumetric
Notes: <number>

## Slide 4: Surface/Volumetric Examinations
Surface examinations indicate the presence of discontinuities on the surface of an article
  Typical inspection methods: liquid penetrant, magnetic particle, eddy current
Volumetric examinations indicate the presence of discontinuities throughout the volume of the article
  May be conducted from either the inside or outside of the component
  Typical inspection methods: radiography, ultrasonic testing, eddy current (for thin tubing or plates)
Notes: <number>

## Slide 5: Visual Examination
Definition: A nondestructive examination method used to evaluate an item by observation.
Used to determine the surface condition of an article, alignment of mating surfaces, compliance with physical requirements (dimensions, settings), etc.
Usually the first method employed for locating suspected defects
Also the oldest and most commonly used NDT method
Notes: <number>

## Slide 6: Why Visual Examination?
Can be used to inspect for surface-breaking discontinuities:
  Cracks
  Holes
  Corrosion
Does not require special equipment other than good eyesight (optical and mechanical aids optional to improve inspection quality)
Low cost
Notes: <number>

## Slide 7: Some Key Terminology
Specification
Procedure
Standard
Regulation
Code

## Slide 8: Specification Vs. Procedure
Specification: An explicit set of requirements to be satisfied by a material, product, or service.
  If a material, product or service fails to meet one or more of the applicable specifications, it may be referred to as being out of specification (OOS)
Procedure: Standardized and documented process for performing an experiment or conducting an evaluation.

## Slide 9: Standard – Two Definitions
Artifact that serves as a basis for comparison; a reference against which other things can be evaluated or calibrated. Official U.S. Time
A set of technical definitions and guidelines that function as instructions for designers, manufacturers, operators, or users of equipment.

## Slide 10: Regulation Vs. Code
Regulation: A principle, rule, or law designed to control or govern behavior.
Code:
  A systematic collection of regulations and rules of procedure or conduct.
  A standard that has been adopted by one or more governmental bodies and is enforceable by law, or when it has been incorporated into a business contract.
    - Example: ASME Boiler & Pressure Vessel Code

## Slide 11: More Common Terminology
discontinuity – an interruption in the normal physical structure of an article (ex. cracks, seams, porosity)
defect – a discontinuity that interferes with the usefulness of the article
  *All defects are discontinuities, but not all discontinuities are defects!!
Notes: <number>

## Slide 12: More Terminology
relevant condition – a condition that requires supplemental examination, corrective measure, or analytical evaluation
evaluation – the process of determining the significance of examination results through the comparison of those results with applicable acceptance criteria
  to determine whether an article is acceptable, salvageable (can be repaired), or rejectable
  Is a “small” imperfection acceptable?
Notes: <number>

## Slide 13: VT-1, VT-2, VT-3
VT-1: Exams conducted to detect discontinuities on the surface of components (“specific exam”)
VT-2: Exams conducted to detect evidence of leakage from pressure retaining components (tanks, pipes, etc.)
VT-3: Exams conducted to determine the general mechanical and structural condition of components and their supports (“general exam”)
    Verification of clearances and settings
    Inspection for loose or missing parts
Notes: <number>

## Slide 14: Inspection Requirements
Usually requires a written procedure that outlines the following:
Type of exam to be performed (VT-1 or VT-3)
Illumination requirements (ex. 50 foot-candles)
  1 foot candle is equal to the amount of light given off by a standard candle at a distance of 1 foot
Surface preparation requirements
Acceptance criteria
Inspection interval (how often inspection must occur)
Required test documentation
Notes: <number>

## Slide 15: Direct vs. Remote
Direct visual exams usually occur within 24” of the surface to be examined
  may use mirrors or magnifying lenses
Remote visual exams performed in areas that are inaccessible for direct examination (inside of pipes and tanks or in hazardous or radioactive areas)
Notes: <number>

## Slide 16: Optical Aids
Used when direct visual examination is not possible
  Microscopes
  Borescopes
  Fiberscopes
  Video Cameras
Notes: <number>

## Slide 17: Mechanical Aids
Micrometers
Calipers
Depth gauges
Thread pitch gauges
Feeler gauges
Weld gauges
Notes: <number>

## Slide 18: Certification Requirements
Certification Level | Training (hrs) | Minimum Experience in Method (hrs) | Minimum Experience in NDT (hrs)
I | 8 | 70 | 170
II | 16 | 140 | 230
Totals: | 24 | 210 | 400
Per ASNT Recommended Practice No. SNT-TC-1A, 2011 edition:
Level I – Trainee
Level II – More experienced
Level III – Highest certification
Notes: <number>

## Slide 19: Certification Requirements, Continued
Must also pass annual eye exams for:
  Near vision acuity (sharpness of vision) – Jaeger chart Example Jaeger Chart
  Far vision acuity – Snellen chart Example Snellen Chart
  Color vision – Ishihara http://colorvisiontesting.com/ishihara.htm
  Note the human eye can generally detect flaws 0.25” or greater
Notes: <number>

## Slide 20: Assignments…
Using Calipers/Micrometers
Perform a Visual Inspection!
*Reference: ASME BPVC Section V, Article 9, Visual Examination
Notes: <number>