## Slide 1
ACADs (08-006) Covered
Keywords
Troubleshooting
Description
Supporting Material
5.1.2.1.4 |  |  |  |  |  |  | 
Notes: <number>

## Slide 2
Objective: Identify and discuss troubleshooting techniques and guidelines

## Slide 3
THE PROCESS OF TROUBLESHOOTING
1. You have to understand the system/component/equipment/circuit (SCEC) enough to troubleshoot it.
2. You have to understand the problem.
3. Create a list of everything and anything that could cause the problem.
4. Observe and record what the SCEC is telling you.
5. Remove items from the list based on what the SCEC is telling you.
6. Develop a troubleshooting game plan based on what is left on the list.
7. Troubleshoot.
8. Fix the problem.

## Slide 4
You have to understand the system, component, or equipment (SCEC) enough to troubleshoot it.
You do not have to understand every part of the SCEC, just the part or piece you are working on, to adequately troubleshoot it. What is it supposed to do, and not supposed to do. Consider what others have to say (Operators, Engineers, other disciplines). Maintain a log, or history of the SCEC. Verify you have the correct information/references (prints, VTM’s, VTD’s, ETC.) required for troubleshooting.

## Slide 5
You have to understand the problem.
Never presume or assume anything. Try to recreate the problem unless there is a safety or equipment concern. Never rule out having more than one problem. Go directly to the source, if possible, for an exact description of the problem (everything seen, heard, smelled, or felt). The perceived problem is actually the SCEC responding to the real problem

## Slide 6
Create a list of everything and anything that could cause the problem.
Anything is possible, not everything is probable. Identify the easiest things to check/troubleshoot. Identify the weak links in the SCEC, the things that are supposed to fail first (breakers open/fuses blown/ETC.). Identify any parts/components recently replaced/repaired or adjusted. Could be wrong part, installed wrong, maladjusted, infant mortality, ETC.

## Slide 7
Observe and record what the SCEC is telling you.
Indicating lights, equipment position, alarms, computer points, annunciators, ETC.
Remove items on the list based on what the SCEC is telling you.
Example: If lights are illuminated, it might indicate that control power is available indicating the control power circuit breaker or fuse is good.

## Slide 8
Develop a troubleshooting game plan based on what is left on the list.
Break the SCEC into manageable pieces or natural breaks. Identify whether you are T/S a symptom or the problem. Take physical location into consideration when determining what and where to troubleshoot. Consolidate T/S steps if possible. Identify the easiest things to check/troubleshoot. If a system is ungrounded you cannot use ground as a reference for voltage measurements, you must use a “known” value. Contacts in series usually STOP something Contacts in parallel usually START something.

## Slide 9
Troubleshooting
Perform a thorough visual inspection using as many senses as applicable. Follow a logical sequence, don’t skip around. Follow Standards and Expectations and comply with procedures, and work order steps. Gather as much information as you can before you change or manipulate anything (preserve “Root Cause of Failure” info).

## Slide 10
Troubleshooting
When taking readings (voltage/resistance) verify you are not being affected by another part of the circuit. Verify all test devices, M&TE and leads are good. Record steps/data/conditions as you T/S. Notify Operations of all T/S activities and any effects it will have on the plant. Make appropriate notifications to protect other people working in the area. Ensure to use all PPE/EPE while troubleshooting.

## Slide 11
Fix the problem.
Ensure that a new problem is not introduced through the troubleshooting process. Ensure the retest adequately verifies the SCEC has been restored to original configuration. Verify new parts are the right ones and good/tested before installing them.

## Slide 12
T/S PROBLEM

## Slide 13
PROBLEM
Operations says that when circuit breaker NANS02D is closed the sump pump does not start.
CONDITIONS
Breaker NANS02D is open, the MCC breaker is closed, the green light on the MCC is lit (normal brilliance) and Operations can start the sump with handswitch CS1.

## Slide 14
R
G
74
Res - R
Res - G
62 TDD
42 a
42 b
252 a
L1
L2
49
42
74
62 TDO 1 min
CS1 START
125vac
X1
U
1
2
2.5 Amp
CS1 AUTO
LSHH
227
AX
AX
LO - LO

## Slide 15
Bad wires (open) Bad terminations (not making contact) MCC power stabs are bad (not making contact) MCC Circuit breaker is open Control transformer is bad Control power fuse is blown AX contact is bad (high resistance/open) LO – LO contact is bad (high resistance/open) 42 coil is bad (open) 49 contact is bad (high resistance/open) 252 contact is bad (high resistance/open) 62 coil is bad (open) 62 contact is bad (high resistance/open) MCC control power stabs are bad (not making contact)
PROBLEM LIST

## Slide 16
What do we know?
CONDITIONS
Breaker NANS02D is open, the MCC breaker is closed, the green MCC light is lit (normal brilliance) and Operations can start the sump with handswitch CS1.

## Slide 17
Bad wires (open) Bad terminations (not making contact) MCC power stabs are bad (not making contact) MCC Circuit breaker is open Control transformer is bad Control power fuse is blown AX contact is bad (high resistance/open) LO – LO contact is bad (high resistance/open) 42 coil is bad (open) 49 contact is bad (high resistance/open) 252 contact is bad (high resistance/open) MCC control power stabs are bad (not making contact) 62 coil is bad (open) 62 contact is bad (high resistance/open) = Possible but not probable
PROBLEM LIST

## Slide 18
TROUBLESHOOTING GAMEPLAN
1. Have Operations close breaker NANS02D 2. Take a voltage reading across Pts. 1/2 inside MCC You expect 0 volts AC 3. Take a voltage reading across 62 relay coil You expect 120 volts AC 4. Take a voltage reading across 62 relay contacts You expect 0 volts AC

## Slide 19
R
G
74
Res - R
Res - G
62 TDD
42 a
42 b
252 a
L1
L2
49
42
74
62 TDO 1 min
CS1 START
125vac
X1
U
1
2
2.5 Amp
CS1 AUTO
LSHH
227
AX
AX
LO - LO

## Slide 20
R
G
74
Res - R
Res - G
62 TDD
42 a
42 b
252 a
L1
L2
49
42
74
62 TDO 1 min
CS1 START
125vac
X1
U
1
2
2.5 Amp
CS1 AUTO
LSHH
227
AX
AX
LO - LO
V
V
V

## Slide 21
T/S PROBLEM

## Slide 22
Problem Description The Oily Waste Separator sump is overflowing Can you go take a look at It?
What is it? Where is it?

## Slide 23
Look at the STM (System Training Manual) for that system “V” drive/Training/STM/System what system do you think it would be?
Oily Waste = OW

## Slide 28
Dwg. 13-P-OOB-0001 GENERAL ARRANGEMENT POWER BLOCK SITE PLAN

## Slide 30
Where is P08A/B?
In the north yard
What are the two MCC’s involved and where are they?
M08 (Turbine 100’ SW corner) M11 (Turbine 100’ E of Aux. Fd pump)
What is the elementary print?
01-E-OWB-0008

## Slide 31
What do you do?
2. Perform a visual inspection of the MCC’s What do you expect to see?
1. Review the Elementary
Could this account for the problem?
Both MCC’s have red light indication. Scenario #1 MCC M1113 has red indication. MCC M0812 has bright green indication.

## Slide 32
1
2
3
0_-E-OWB-0008

## Slide 33
The motor is not energized The main Cktbrk is closed (green light) Contactor 42-2 is not picked up (green light) Relay 74-2 is de-energized (bright green light) The control transformer/fuse are good (green light) The overload contact has tripped (bright green light)
What does this condition tell you?
Verify that 42-2 is dropped out at M08 and that the 49 contact is open

## Slide 34
Possible Problem
An open “Overload” contact means the motor current has exceeded the rating of the heaters Possible motor or pump problem Motor/Pump Bearings Pump bound up With Proper Document Remove heaters, reset the O/L, and verify that the control circuit works per design.

## Slide 35
Scenario #2 MCC M1113 has red indication. MCC M0812 has green indication.
What does this condition tell you?
The motor is not energized (green light) The main Cktbrk is closed (green light) Contactor 42-2 is not picked up (green light) Relay 74-2 is energized (dim green light) Overload relay is not tripped (dim green light) The control transformer/fuse are good (green light)

## Slide 36
Could coil 42-2 be bad?
QUESTION why would 42-2 not be picked up?
Yes
Could contact AY be open?
Yes
Could contact CS-2 Auto be open?
Yes
Could contact AX be open?
Yes
Could coil AX be bad?
Yes, The other pump could be running because of the alternator circuit
Could coil AY be bad?
Don’t Know, It’s not energized
Could contact LSHH - 14 be open?
Yes The other pump could be running because of the alternator circuit

## Slide 37
Contact AX should be closed (Hi/Hi condition) AX coil should be energized (Hi/Hi condition) Contact LSHH - 14 (2/3) should be closed (Hi/Hi condition) Contact CS-2 contact (3/4) should be closed (system in Auto) Contact AY should be closed (no Lo/Lo condition)
Could the sister motor be energized without AX coil being energized?
Yes, through the alternator
WHAT TO CHECK?

## Slide 39
Total Res. = 350 Ohms R1 + R2 + R3
Total Current = .05A 17.5/350
Voltage drop = 1.5 (I X R)
Voltage drop = 6 (I X R)
Voltage drop = 10 (I X R)
R1
R2
R3
Total Voltage = E1 (1.5) + E2 (6) + E3 (10) = E total (17.5)

## Slide 40
1.5 VDC
6 VDC
10 VDC

## Slide 41
OPEN
17.5VDC
0 VDC
0 VDC

## Slide 42
125 VDC COIL

## Slide 43
Resistance
125 VDC COIL
+
+
-
-
-
-

## Slide 44
POS
NEG
NO VOLTAGE READING
135 VDC
+
-
+
+
NO RESISTANCE
135VDC

## Slide 45
NEG
POS
NO VOLTAGE READING
VOLTAGE DROP
VOLTAGE DROP
+
-
+
-
135VDC

## Slide 46
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5

## Slide 47
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5
VM1
VM2
VM3
VM4
SPRINGS FAIL TO CHARGE
Check the following components 52/IS 52/SMLS 52/CLMS Motor

## Slide 48
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5
VM7
VM9
VM10
VM11
VM12
VM13
Springs charge Brkr. won’t close
Check the following components 52/IS 52Y 52Y 52 52X 52SMLS

## Slide 49
1
2
3
4
0_-E-LOB-0003

## Slide 50
0_-E-NAB-0021

## Slide 51
480V
120V
G
42 b
CS-1
CR
AX
CR
42
49
74
LSHH
AX
2.5A
74

## Slide 52
480V
120V
G
42 b
CS-1
CR
AX
CR
42
49
74
LSHH
AX
2.5A
74

## Slide 56
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5

## Slide 57
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5
VM1
VM2
VM3
VM5
VM4
VM6
VM7
VM8
VM9
VM10
VM11
VM12
VM13

## Slide 58
M
52Y
52X
52
52Y
52Y
52 IS
52 IS
52Y
52 SMLS
52 SMLS
52 SMLS
52 CLMS
4
2
3
1
8
3
4
1
1
1
1
1
4
8
7
9
3
2
4
2
1
6
10
2
3
2
2
1C
1
2
5

## Slide 59
«
«
«
M

## Slide 60
TROUBLESHOOTING !!!

## Slide 61
The process of detecting a problem, determining its cause, and taking corrective actions.

## Slide 62
5 major steps of T/S 1. Identify the problem: Recognizing that a problem exists and observing its symptoms. A. Visual/audio warnings B. Automatic shutdowns C. A signal value not within its normal range 2. Take preventive action: A short term action that is meant to put a circuit in a safe condition while work is performed to correct the problem. A. Initiate an emergency shutdown B. Switch the circuit from automatic to manual control C. Bypass a piece of equipment D. Use a piece of backup equipment

## Slide 63
3. Determine the cause of the problem: A process of elimination. Separating those factors that are not causing the problem from those that might be causing the problem. A. Was the change in the circuits operation abrupt or gradual B. Is the problem intermittent or constant C. Have there been similar problems in the past D. Did the problem occur while the circuit was in a steady-state condition, or was the circuit in startup or shutdown. Sources of information: A. Prints/diagrams B. Experience (electricians and operators) C. Supervision Two commonly used methods of elimination: A. Serial method: Checking components in sequence one at a time. B. Half-splitting method: Splitting the circuit in half again and again following the readings to where the problem is.

## Slide 64
4. Correct the problem: Making adjustments and repairing or replacing equipment. 5. Return the circuit to normal operation: Reverse any preventative actions and ensuring the circuit operates properly (retest).

## Slide 66
480 VAC
120 VAC
VM = 120VAC
VM
VM

## Slide 67
480VAC
120VAC
OPEN
VM = 120VAC
VM

## Slide 68
VM
VM = 120VAC
480 – 120VAC

## Slide 69
480 – 120VAC
VM1
VM3
VM2
VM1 + VM2 + VM3 = 120VAC

## Slide 70
VM1
VM1 = 0VAC
VM2
480 – 120VAC
VM3
VM2 = 120VAC
VM3 = 0VAC
VM5
VM4
VM4 = 120VAC
VM5 = 0VAC

## Slide 71
VM1
VM1 = 120VAC
VM2
480 – 120VAC
VM3
VM2 = 0VAC
VM3 = 0VAC
VM5
VM4
VM4 = 120VAC
VM5 = 0VAC

## Slide 72
VM1
VM1 = 0VAC
VM2
480 – 120VAC
VM3
VM2 = 0VAC
VM3 = 120VAC
VM5
VM4
VM4 = 120VAC
VM5 = 120VAC

## Slide 73
480 – 120VAC
E1
E3
E2
E4
ET = E1+ (E2 = E3 = coil) + E4
VM
VM
VM
VM
VM

## Slide 74
Will the relay coil be picked up?
Will the lights be lit?

## Slide 75
480V
120V
G
42 b
CS-1
CR
AX
CR
42
49
74
LSHH
AX
2.5A
74
LSHH = Automatic Start
CS-1 = Manual Start
CR = Control Relay
42 = Main Contactor
74 = Alarm Relay
AX = Auxiliary Relay
49 = Overload Contact

## Slide 76
A
A
B
B
C
C
Pt.’s A Pt.’s B Pt.’s C
120VAC
0VAC
0VAC

## Slide 77
T/S PROBLEM

## Slide 78
REVIEW PRINT 01-E-SGB-0001

## Slide 79
PROBLEM:
Operations can not close valve SGAUV134 in Override The Override lights are lit

## Slide 80
What major components does this print show us?
What does the “Override” function do? How does Operations activate the “Override’ function? What “Safety” signal(s) is Operations “Overriding”? What does taking the circuit to “Override” allow Operations to do to valve SGAUV0134?
SGAUV0134 – DC Motor SGAUV0134A – DC Solenoid
Defeats a “Safety” actuation before the signal has cleared
By taking CS-1/2 to the “Open” position
AFAS – 1 AFAS – 2
To close it

## Slide 81
After solenoid SGAUV134A is energized how long does it take to start changing valve SGAUV134?
What stops the motor when the valve is opening? If the “Safety” signal has cleared can you still go to “Override”? Where is CS-2 physically located at? What contact allows the positive DC to the motor in either direction?
tqo switch (torque open switch)
27 seconds
No
_JZJAE01 (Remote Shutdown Panel)
42M

## Slide 82
What are the possible problems?
Bad CS-1 contact Bad OR contact Bad 42 – 2a contact Bad 42 – 1c coil Bad 42 – 2c coil
What do you check?