## Slide 1
ACADs (08-006) Covered
Keywords
Half-splitting, bracketing, change analysis, end-to-end, linear, Kepner-Tregoe, failure analysis, intuitive, correlation, intermittent.
Description
Supporting Material
5.1.2.1.4 |  |  |  |  |  |  | 
Notes: <number>

## Slide 2: Systematic Troubleshooting
A thinking skill
Nearly everyone can troubleshoot
Some do it better than others. Why?
Mental State
Humility versus Confidence
What does good troubleshooting look like?
Quick, accurate & consistent
Notes: <number>
A thinking skill
shaky ground here
Nearly everyone can troubleshoot
Some better than others, some faster, less random, more direct
Some do it better than others. Why?
Mental State
You must get your mind right before troubleshooting. If you think you already know what the problem is, you’re not being systematic
Humility versus Confidence
Can’t be too confident. You can’t be too humble
What does good troubleshooting look like?
Quick, accurate & consistent

## Slide 3
Start
Is it broke?
Can you blame
Someone?
Does anyone
know?
Did you mess
With it?
You moron!
Sucks to
Be you.
Hide it.
End
Don’t mess
with it.
Then do it.
No problem
No
No
Yes
Yes
No
Yes
Yes
No

## Slide 4: Troubleshooting Methods
Systematic Methods
Half-splitting
Bracketing
Change analysis
End-to-end or linear
Kepner-Tregoe (KT)
Failure analysis
Non-Systematic Methods
Intuitive method
Shotgun troubleshooting
Easter egging
Notes: <number>
Compare and contrast systematic versus non-systematic troubleshooting methods

## Slide 5: Non-Systematic Troubleshooting methods
The Intuitive or Experience approach
  “I know what’s wrong! I’ve seen this before”
Shotgun approach
  Arbitrarily replacing all replaceable components within a system in no logical sequence
Easter-egging
  replacing unrelated components more or less at random in hopes that a malfunction will go away
“Something must be done”
  The problem no longer exists, but we must document that we fixed something
Notes: <number>
Non-systematic methods and some examples
The Intuitive or Experience approach
  Used often by experienced people on problems they’ve seen before. Can be quite reliable for recognized symptoms but is not systematic.
Shotgun approach
  Shotgun Metaphor
  There's a fine line between replacing good parts to make repair more efficient, as opposed to replacing good parts because of incompetence
Easter-egging
You probably won’t find all the eggs
“Something must be done”
  Often management driven or culture driven

## Slide 6: Systematic Troubleshooting Methods
System Verification -or- end to end
Change Analysis
Root Cause or Failure Analysis
Kepner-Tregoe (KT) Analytical Troubleshooting® (ATS)
Bracketing –or- Half Splitting –or- diagnosis by division
Notes: <number>
System Verification
  Start at one end and verify every component and connection
Change Analysis
  Determine conditions before and after problem, then determine what changed that may have caused the problem
Root Cause or Failure Analysis
  Usually used by engineering
Kepner-Tregoe (KT) Analytical Troubleshooting® (ATS)
  Copyrighted system for problem solving in any system, not just technical systems
Bracketing –or- Half Splitting –or- diagnosis by division
  Most often used by technicians

## Slide 7: Kepner-Tregoe (KT) Analytical Troubleshooting® (ATS)
State what the problem is,
Describe the problem in detail,
Develop possible causes,
Test possible cause against the problem description,
Verify the most probable cause,
Select a fix, and finally
Identify other places that may need the same fix.
Notes: <number>
Copyrighted system
Used to be taught by Doug Doty (RIP)

## Slide 8: Bracketing, Half splitting, or Diagnosis by division
Intuitive diagnosis by division often results in circular troubleshooting and skipped steps, both of which decrease effectiveness
Diagnosis by division works only when the Troubleshooter keeps track of what he's ruled out and what he hasn't.
Notes: <number>
Put a bracket on a known good spot and another bracket on a known bad spot, then move the brackets keeping one on good an the other on bad until there is only one component between the brackets
Half split – each step splits the circuit in half. At each step you determine in which direction the problem lies.
Divide and conquer
Diagnosis by division – same as half splitting

## Slide 9: Four Steps of Systematic Troubleshooting
Determine the symptoms
Localize to a functional unit
Isolate to a circuit
Locate specific trouble

## Slide 10: 1. Determine Symptoms
You must know what is happening before you can determine why it’s happening
Based on observations
Requires some knowledge of how the equipment normally works
Normal system manipulation may be required
Comparisons between good and bad channels may be valuable
Every attempt should be made to determine the nature of the fault through passive means

## Slide 11: 2. Localize to a functional unit
Use system drawings, functional block diagrams, big picture information sources
Based on symptoms
Test equipment not used at this point
Requires reasoning; which functional blocks could be causing the problem?
Eliminates functional units from consideration

## Slide 12: 3. Isolate to a local circuit
Use prints, schematics, tech manual and more detailed technical sources
Use test equipment extensively to determine inputs and outputs
Abnormal system manipulations may be needed

## Slide 13: 4. Locate Specific Trouble
Use prints, schematics, tech manual and the most detailed technical sources
Use test equipment extensively to isolate down to the component level
Requires detailed knowledge of system internal operation, circuit operation, signal tracing
Frequently done in the rework facility

## Slide 14: Characteristics of good troubleshooting
Don’t panic. Don’t freak out.
Keep track of what you have checked
Start at one place, deal with one symptom, then move on
Avoid random checks. Be purposeful
Before making a check, say out loud what you expect to find if the system were working.
Once you check something, say out loud what the deviation was between what you saw and what you expected
Understand what usually causes problems
  Human error
  Misconfiguration
  Component failure

## Slide 15: Intermittent problems
Problems that are not reliably reproducible
Single occurrence
Very infrequently
Occurs occasionally
Occurs frequently
Reproducable
Notes: <number>
the better you get at troubleshooting, the more intermittents you see

## Slide 16: Strategies for dealing with intermittent problems
Ignore it until it becomes reproducable
Statistical analysis – look for correlations
  Graph ERFDADS historical trends
Preventive maintenance / general maintenance
Shotgun approach
Turn the intermittent into a reproducable problem (Break the most likely thing, then replace it)
FIN - Wait 30 days then send it back to I&C

## Slide 17: Correlation
“Every time it rains we get ground alarms”
“Every time we start ‘E’ charging pump, indication on source range ‘C’ goes away.”
Correlated once
Correlates occasionally
Correlates sporadically
Correlates reliably

## Slide 18: Correlation is not causation
Once is not a trend.
Twice is not always.

## Slide 19: Troubleshooting Exercises
Retro
encabulator
unilateral phase
detractors
Hydrocoptic
marzel vanes
Synchronizing
cardinal
grammeters
Differential
girdlespring

## Slide 20: Foxboro 743CB Digital Controller

## Slide 23: Foxboro 743CB Digital Controller
Input: 4-20ma, 1-5VDC, 1-9999 Hz pulses, or contact input
Output: 4-20ma, 1-5VDC or contact out
Inputs can be conditioned:
  Squared or square root, characterized including for thermocouple, RTD, or lag filtered
Controller can be set up for PID, EXACT auto-tuning, cascade, batch control, alarms, remote or local setpoint, totalizing and dynamic compensation

## Slide 24
Notes: <number>
Setpoint selected using the ‘SEL’ button, controller in automatic using the A/M button

## Slide 25
Notes: <number>
Process input selected using the ‘SEL’ button, Controller in manual using the A/M button

## Slide 26
Notes: <number>
Output selected using the ‘SEL’ button, Controller in automatic using the A/M button