## Slide 1
ACADs (08-006) Covered
Keywords
Foreign material exclusion, electrical divisional separation, electrical physical separation, cable tray layout, wrapping, fire detection, Class 1E electrical distribution.
Description
Supporting Material
1.3.8.1 | 4.20.1.14 | 5.1.2.17 |  |  |  |  | 
Notes: <number>

## Slide 2
<number>
NUET 130 FOREIGN MATERIAL EXCLUSION
PART DEUX
The purpose of this class is to familiarize students with the Foreign Material Exclusion (FME) program.
These sessions will also include reviews of major industry operating experience events tied to FME problems.
Notes: <number>
<number>
<number>
<number>

## Slide 3
<number>
FOREIGN MATERIAL EXCLUSION (FME)
TERMINAL OBJECTIVE
Students will understand the need for and fundamentals of nuclear power plant FME Programs
Notes: <number>
<number>
<number>
<number>

## Slide 4
<number>
ENABLING OBJECTIVES
Describe the concept of electrical divisional separation, including its importance to nuclear safety.
Describe the concept of electrical physical separation, including its importance to nuclear safety.
Describe the concept of cable tray layout and wrapping to ensure limitations on fire damage
Describe the fire detection and mitigation associated with Class 1E electrical distribution.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 5
<number>
Excluding Foreign material from plant systems will help prevent:
Damage to Fuel cladding
Damage to equipment
Degradation of Heat Transfer capability
Increased radiation levels
Increased presence of discrete hot particles
Increased radwaste generation
Degradation of system flow
Unscheduled plant outages and outage extensions
Changes to plant chemistry
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 6
<number>
Good FME control basics will involve:
• Providing training and regular briefings for the workers
• Isolating the work area with a rope or barrier and posting the work area with a sign identifying it as an FME area.
• Pre-inspecting items for loose or faulty components prior to bringing them into FME Control Area
• Keeping foreign materials and tools from entering an open system
• Keeping the area clean and orderly
• Cleaning and inspecting internals prior to closing the system
• Performing pre-inspection of temporary equipment to verify that gaskets, seals, and packings are approved for use at Fermi 2. Examples of temporary equipment are decontamination, flushing, cleaning, and performance monitoring equipment or attachments.
FME Areas should be kept as small as practical.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 7
<number>
Good FME control basics will involve:
• Flange cleaning or gasket removal should be performed prior to removal of plugs.
Tools and materials/parts shall be inspected before items are brought into a FMEA, and during removal from a FMEA, to identify loose or missing parts.
Prior to entering the FMEA, personnel shall remove personal items and/or secure items using lanyards or other appropriate means.
Lanyards should be used on items that could be dropped and lost, could cause damage or be a safety issue. Lanyards provide a backup method for preventing loss of tools and equipment.
Gray or silver tape shall not be used within an FME Area. If lost, recovery of this material would be difficult since it is hard to see underwater against a stainless steel background.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 8
<number>
FOREIGN MATERIAL EXCLUSION (FME)
Good FME control basics will involve:
• Installation materials should not be delivered to the FMEA sooner than required
Components should be assembled so that visual inspection of internals may be performed just prior to closure.
Local cleanup of the area shall be performed as work progresses to preclude the introduction of contaminants into clean systems.
Notes: <number>
<number>
<number>
<number>

## Slide 9
<number>
Duct tape adhesive is easily dissolved by fuel oil and to a lesser extent by oil-based products. Due to the potential loss of the adhesive from the duct tape in contact with fuel oil and/or oil-based products, duct tape should not to be used as an FME cover. The duct tape itself could become foreign material. In those cases where only duct tape can adequately serve as an FME cover, the surface on which the duct tape will adhere to shall be thoroughly cleaned to eliminate fuel oil/oil residue to the extent possible.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 10
<number>
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 11
<number>
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 12
<number>
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 13
<number>
Refuel Floor FME
In addition to standard requirements of the FME procedure, the following FME guidelines are specific to the Refuel Floor. The primary concern on the Refuel Floor is protecting the Reactor Cavity, Spent Fuel Pool (SFP), Dryer Separator Pit (DSP), and the Fuel from adverse chemical and metallic foreign material intrusion. Historically, fuel fretting failures have been caused by ribbon or wire-like metallic elements that get trapped in the fuel bundle and fuel bundle support arrangement. Particular interest will be paid to limiting and controlling processes requiring or generating gasses, liquids, wire strips/wire brushes, grinding/machining debris, nuts, bolts and screws adjacent to, or over, the Refuel Floor FME areas. When these processes are required on the Refuel Floor (prior to performance of the work), it must be demonstrated that materials, tools, or debris generated in the FME area will be controlled such that:
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 14
<number>
Refuel Floor FME
They will be easily identifiable and retrievable underwater.
Will not react with the components or other materials and tools in a manner that will harm fuel or RPV components.
They will not fall or be dropped into the Reactor Cavity, SFP or DSP.
FME practice on the Refuel Floor shall be sequenced and controlled by the Refuel Floor Coordinator (RFC).
If safety conditions, work conditions, or radiological conditions change and affect established FME controls and procedures, the Refuel Floor Coordinator may temporarily modify FME controls and procedures for the Refuel Floor FME Area until conditions return to normal.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 15
<number>
Refuel Floor Buffer Zone: A 3-foot area on the Refuel Floor surrounding the SFP, DSP, and the Reactor Cavity. The area is painted yellow on the floor and is marked with black lettering "FME BUFFER ZONE." This area designates an area of HEIGHTENED FME AWARENESS. Personnel shall avoid entering the buffer zone unless required to complete work activities.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 16
<number>
Main Generator or Recirculation Motor Generator Sets –
Due to the size of the component and the large number of persons involved in generator maintenance, the electrical generator is extremely susceptible to foreign material during maintenance operations. Assignment of FMEA control is required for the main generator whenever the generator and MG Sets are open for maintenance.
Operating Experience Alert!
In 2009 Fermi 2 was shutdown for over a month due to a leak within the main generator stator winding coolant system. The cause of the leak was attributed to a very small piece of metal that got into the coolant system and “fretted” in a location, damaging the coolant tubing inside the stator.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 17
<number>
FME High Risk systems:
- (B21) Main Steam
- (B31) Reactor Recirculation System
- (C11) Control Rod Drive
- (E11) Residual Heat Removal System
- (E21) Core Spray System
- (E41) High Pressure Coolant Injection System (HPCI)
- (E51) Reactor Core Isolation Cooling (RCIC)
- (G33) Reactor Water Cleanup
- (N2100) Reactor Feedwater
- (N2103) Standby Feedwater System
- (N3000S001) Turbine Main Generator
- (P1100) Condensate Storage and Transfer
- Work in or over the Spent Fuel Pool/Cavity/Dryer Separator Pit (when flooded)
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 18
<number>
Other High Risk locations:
- Internal work in the Torus
- Internal work in the Main Turbine / Generator / Exciter
- Internal work in the Main Condensers / Feedwater Heaters / Moisture Separator Reheaters
- Internal work in the Main and Auxiliary Transformers (including isophase bus duct)
- Internals of Emergency Diesel Generator
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 19
<number>
PROCEDURE:
Discuss Section 4 of Conduct Manual MMA17
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 20
<number>
FOREIGN MATERIAL EXCLUSION (FME)
TERMINAL OBJECTIVE
Students will understand the need for and fundamentals of nuclear power plant FME Programs
Notes: <number>
<number>
<number>
<number>

## Slide 21
<number>
ENABLING OBJECTIVES
Describe the concept of electrical divisional separation, including its importance to nuclear safety.
Describe the concept of electrical physical separation, including its importance to nuclear safety.
Describe the concept of cable tray layout and wrapping to ensure limitations on fire damage
Describe the fire detection and mitigation associated with Class 1E electrical distribution.
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>

## Slide 22
<number>
QUESTIONS ???????????
FOREIGN MATERIAL EXCLUSION (FME)
Notes: <number>
<number>
<number>
<number>