## Slide 1
ACADs (08-006) Covered
Keywords
Safety tagging, clearance.
Description
Supporting Material
5.1.2.1.1 |  |  |  |  |  |  | 
Notes: <number>

## Slide 2
<number>
NUET 130 Safety Tagging / Clearances
The purpose of this class is to familiarize students with the process to provide electrical and mechanical protection to workers.
This sessions will also include reviews of major industry operating experience events tied to inadequate protection.
Notes: <number>
<number>
<number>
<number>

## Slide 3
<number>
SAFETY TAGGING
TERMINAL OBJECTIVE
Students will understand the need for and fundamentals of power plant safety tagging
Notes: <number>
<number>
<number>
<number>

## Slide 4
<number>
ENABLING OBJECTIVES
Describe the concept of hazardous energy sources.
Describe the process for establishing electrical protection boundaries.
Describe the process for establishing mechanical protection boundaries.
Describe the process to create a protection contract between workers and the operating authority
Students will be familiar with the procedure used to hang and verify safety tags
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>

## Slide 5
<number>
SAFETY TAGGING
Tagging related definitions:
Additional Measures - An additional means taken, during Clearance Tagouts, to prevent inadvertent operation of equipment or reduce the likelihood of inadvertent energizing.
Crew member - One of a group of individuals who perform job tasks at plant sites and works under the direction of a Job Leader and under the protection of a Protection Leader
Drains - Grounds used to remove charges retained in lines and equipment after deenergization.
Grounds - Conducting connections between lines or equipment being worked on and earth to provide protection against foreign voltages.
Notes: <number>
<number>
<number>
<number>

## Slide 6
<number>
SAFETY TAGGING
Tagging related definitions:
Additional Measures - An additional means taken, during Clearance Tagouts, to prevent inadvertent operation of equipment or reduce the likelihood of inadvertent energizing.
Crew member - One of a group of individuals who perform job tasks at plant sites and works under the direction of a Job Leader and under the protection of a Protection Leader
Drains - Grounds used to remove charges retained in lines and equipment after deenergization.
Grounds - Conducting connections between lines or equipment being worked on and earth to provide protection against foreign voltages.
Notes: <number>
<number>
<number>
<number>

## Slide 7
<number>
SAFETY TAGGING
Tagging related definitions:
Crew Member Record (CMR) - The form used daily and maintained by a Protection Leader to record all people working under the applied protection. A CMR must be used whenever there is more than one person on a Work Order and they have Red Tag protection provided. The CMR will provide a means of acknowledgement that the Job Leader and Crew Members have been informed of the protection status for a job prior to commencing work and changes to be made to the protection before they occur. The CMR will remain with the Work Order during the job and will be filed with the Work Order and other associated documents after the completion of the work.
Job Leader - The individual in direct charge of a job or a portion of a major overhaul. In many cases, the Job Leader will also be the Qualified Protection Leader.
Notes: <number>
<number>
<number>
<number>

## Slide 8
<number>
SAFETY TAGGING
Tagging related definitions:
Operating Agent - The person who is qualified to apply protective tagging as the delegate of the Shift Operating Authority or the System Supervisor.
Example: Electrical Maintenance GMJ that is qualified MOP12 and Limited Scope Tagging.
Work Order - A request to perform work on equipment under power plant control. It contains a description of the equipment, job scope, and plant impact. The information on the Work Order shall be sufficient enough so the Operating Authority can provide the appropriate protection.
Work Order Task - A request to perform work on equipment under power plant control. It is normally a part of a Work Order and will have a unique identifying number. The information contained in the Work Order Task shall be sufficient enough so the Operating Authority can provide the appropriate protection.
Notes: <number>
<number>
<number>
<number>

## Slide 9
<number>
SAFETY TAGGING
Tagging related definitions:
Provisional Protection Release - The process used for temporary clearance of protection.
Protection Leader - An individual currently qualified and authorized in the use of the Protective Tagging System, who receives protection on equipment or a system to do work.
Shift Operating Authority - The Shift Manager (SM), or delegate.
Shop order (shop work) - Any work activity that, when performed, does not affect installed plant Systems, Structures or Components and may be performed without SM permission.
Static Drains - Grounds used to remove charges continuously induced in deenergized lines and equipment by nearby energized equipment or from charges induced during oil handling operations. (i.e., filling or recirculation of oil, on transformers rated at 200kVA or over, having a primary or secondary voltage of 13.2kV or higher
Notes: <number>
<number>
<number>
<number>

## Slide 10
<number>
SAFETY TAGGING
Tagging related definitions:
Safety Tagging Record (STR) – The package identifying the exact boundaries of the protection and every tag to be hung along with the required device positions.
Tagging Dots - Tagging dots are an informational placard informing the Operator that there are tags on equipment for which there are controls for in the Main or Radwaste Control Room (or local panels as applicable). They are not treated as Safety or Configuration tags:
RT Dot - The component is controlled by a Red Tag.
CT Dot - The component is controlled by a Caution Tag.
LST Dot -The component is controlled by a Limited Red Tag.
Notes: <number>
<number>
<number>
<number>

## Slide 11
<number>
SAFETY TAGGING
Operations personnel roles:
STR Writer - The STR writer is the person with initial responsibility to define the STR boundary. They may receive input from others in the form of suggested boundaries.
STR Reviewer - The person with the skills and knowledge of a STR writer, who reviews the STR boundary for technical accuracy.
STR Approver - The STR Approver is the representative of the Shift Operating Authority at all steps in the STR and tagging process after the STR is ready to be approved.
STR Positioner - The STR Positioner is the person who actually manipulates components (with the support of others as necessary) and hangs tags. A STR Positioner is usually an Operator qualified at least on the system being tagged out.
STR Verifier - The STR Verifier is the person who verifies the component positions on STR. The STR Verifier is also qualified in accordance with MOP02, Independent Verification.
Notes: <number>
<number>
<number>
<number>

## Slide 12
<number>
SAFETY TAGGING
Protection Leader:
The Protection Leader is the employee and/or business unit delegate or contractor who is qualified to receive protection on equipment or systems to do work and has responsibility for keeping all persons working under this protection informed of the limits of protection, including any changes in the protection that may occur.
Notes: <number>
<number>
<number>
<number>

## Slide 13
<number>
SAFETY TAGGING
General information pertaining to tagging:
Component Positions
STRs should place equipment into positions that is required for protection and restores the equipment to a position that supports necessary recovery of the system.
Example: (1) A locked closed valve, used for protection, should be listed as locked closed on the STR for protection and restored to a locked closed position. (2) A normally open pump suction valve should be listed as closed on the STR for protection, and restored to closed to support fill and vent per SOP if the SOP opens the valve after fill.
Notes: <number>
<number>
<number>
<number>

## Slide 14
<number>
SAFETY TAGGING
General information pertaining to tagging:
Risk Management -
All STRs should be evaluated for Risk. Typical entry conditions for formal Risk Assessment are:
– Entry into permit required confined space.
– Lifting and landing of energized leads for safety related or other potential trip circuits/instruments.
– Activity performed in an environment that requires heat stress stay time greater than 10 minutes.
– Is in a High Radiation Area or Locked High Radiation Area.
– Is in a High Contamination Area or Airborne Area.
– Entry into a less than 8-hour Technical Specification/Allowed Out of Service Time (AOT).
– Loss of single train of Spent Fuel Pool (SFP) cooling.
– TBCCW or RBCCW pump maintenance that either removes them from service or involves instrumentation that could cause a trip.
Notes: <number>
<number>
<number>
<number>

## Slide 15
<number>
SAFETY TAGGING
General information pertaining to tagging:
Work on Red Tagged components –
When work on equipment that is tagged will not affect the isolation capability of that equipment and Shift Operating Authority concurs, then work may be performed on that equipment.
Electrical isolation devices tagged in the OFF or equivalent position may have their door/cover opened by qualified individuals and maintenance performed provided the device remains in its tagged position.
Examples of work on tagged components:
– A vent or drain valve tagged closed may have the outlet weld repaired.– – A Motor Operated Valve (MOV) with the hand wheel tagged closed may have electrical work performed that will not cause the valve stem to be moved.
– A blocked or gagged device may be worked on if the work will not affect the isolation ability of the block or valve.
– Valve stem lubrications that will not cause the valve stem to be moved
Notes: <number>
<number>
<number>
<number>

## Slide 16
<number>
SAFETY TAGGING
General information pertaining to tagging:
High Radiation Area Tagging
Handwheel tags for MOVs in High Radiation areas may be placed on the associated High Radiation boundary doors provided that the valve has been positioned and verified remotely and the door is closed and locked with key under the control of the Shift Manager / Radiation Protection IAW MRP06, Accessing High Radiation, Locked High Radiation and Very High Radiation Areas, with no need for personnel entry.
Primary Containment Isolation Valves
The penetration flow path must be isolated with a manual valve, blank flange, or active valve de-energized in the closed position. The redundant valve shall be used to provide this isolation. The motive force (air, motor) shall be tagged. This should be documented on an STR
Notes: <number>
<number>
<number>
<number>

## Slide 17
<number>
SAFETY TAGGING
General mechanical information pertaining to tagging:
Plug, Line Stop and Freeze Seals
1. When plugs/line stops are used as an isolation point to perform work, then the following are required:
Plugs/line stops shall be installed under approved procedures or work instructions in a Work Order activity.
Plugs/line stops shall be determined to be seated and one of the following shall apply:
– The plug is provided with a constant gas/water supply to remain inflated and either the supply or the plug/line stop is tagged with a Red Tag.
– A physical locking/jacking device is installed and the device is tagged with a Red Tag.
Notes: <number>
<number>
<number>
<number>

## Slide 18
<number>
SAFETY TAGGING
General mechanical information pertaining to tagging:
Plug, Line Stop and Freeze Seals
2. When a freeze seal is used as an isolation point to perform work, then the following are required:
Freeze seals shall be performed by approved procedures and controlled by work instructions in a Work Order activity.
A Clearance Tagout shall be placed to control the other isolation boundaries associated with the freeze seal.
Freeze seals shall be tagged on the freeze seal control injection station.
The Clearance Tagout Positioner and Verifier shall verify freeze seal in place by review of maintenance freeze seal procedure
Notes: <number>
<number>
<number>
<number>

## Slide 19
<number>
SAFETY TAGGING
General electrical information pertaining to tagging:
Potential below 50 volts does not require Red Tag Protection.
Potential below 50 volts (RMS) does not require Red Tag Protection
Electrical Shock Prevention
In order to provide effective electrical shock hazard protection, all power supplies feeding the component to be worked must be identified.
If questions arise or there is doubt of the accuracy of the document the following action may have to be taken.
• The existence of energy controlling devices (i.e. photocells, isolation contactors, thermostats, etc.) must be considered and evaluated when determining the method for providing a positive means to determine if the circuit is properly deenergized for a component.
Notes: <number>
<number>
<number>
<number>

## Slide 20
<number>
SAFETY TAGGING
General electrical information pertaining to tagging:
When adequate prints do not exist to determine all component power supplies, a component walkdown should be performed to determine the supply. Additionally use of a positive means to determine if the component is deenergized will be used prior to permitting a protection contract to be established. For example a plant lighting circuit may be verified by ensuring the correct light is extinguished when it power supply breaker is turned off or Live/Dead/Live check at the component to be worked performed before and after turning power off to ensure proper power supplies are identified. The method used will be documented in the comments section of the STR.
Notes: <number>
<number>
<number>
<number>

## Slide 21
<number>
SAFETY TAGGING
Documentation of the Protective Tagging events, near misses and low level precursors :
Severity Level | Remaining Barriers | Examples
1 | None | Unexpected energy is found by the workers inside the protection boundary after the Protection Contract is in effect. While work is in progress, the protection boundary is found to be inadequate. Work is conducted outside of a protection boundary (e.g., wrong component is worked). Manipulation of a tagged component.
2 | One - A problem with a protection boundary is discovered after the Work Order or Work Order Task is released. The remaining barrier is the validation of adequate protection by the Protection Leader prior to sign on to the protection. | Tags hung on wrong component; therefore the planned boundary is not intact; discovered before maintenance signs on. Maintenance walkdown of the tags identifies an unknown hazard present before maintenance signs on. Worker at work but not signed on to a adequate protection. Protection released while work still in progress (Protection not removed).
Notes: <number>
<number>
<number>
<number>

## Slide 22
<number>
SAFETY TAGGING
Severity Level | Remaining Barriers | Examples
3 | Two - A problem with a proposed protection boundary is discovered while the STR is not yet approved for implementation. Approver and Protection Leader are independent barriers that have not yet been breached. | Work Order inadequately describes what needs to be tagged. STR written found by verifier, craft review, or approver to be incomplete. Tag hung on wrong component discovered during the IV process before the contract is available to maintenance.
Trend Only 4 | N/A | Labeling issues, drawing issues interfere with STR preparation STR's not prepared prior to T-6 Missed process steps, paperwork rejected for re­assessment. Coordination issues (e.g., schedule milestones not met) Work Orders that remain in the schedule after scope freeze that are not planned or have parts issues resulting in removal after schedule freeze. Protection Contract not signed off at end of day. Protection Contract not released at the completion of work. Tagging Program Enhancement
Documentation of the Protective Tagging events, near misses and low level precursors :
Notes: <number>
<number>
<number>
<number>

## Slide 23
<number>
SAFETY TAGGING
Unprotected Work :
Long-standing practice in the nuclear electric generating industry has shown that many routine work activities are safely and properly performed on equipment where the individual conducting the work is certainly in a position to prevent the unexpected release of energy to that worker. It is precisely because the risk of unexpected release of energy is essentially precluded that OSHA does not require lockout/Tagout in these cases. The following list is not all inclusive and items should be added as they are identified by submitting a CARD. Examples Of Work Allowed Without Tags:
  Surveillance and Performance Test activities (SST and PST events) do not require Protective Tagging unless specified on their respective authorization forms or within the body of the respective procedure.
  No energy source present or possible
  Equipment that is not hard wired provided the power sources is disconnected (i.e., unplugged) within sight of the worker.
Notes: <number>
<number>
<number>
<number>

## Slide 24
<number>
SAFETY TAGGING
Unprotected Work :
  Change light bulbs
  Cleaning/replacing on clean side ventilation filters where the worker is not exposed to rotating machinery
  Portable equipment repairs
  With proper Operations approval, opening electrical panels in accordance with standard electrical safety precautions
  Troubleshooting electrical equipment using standard electrical safety precautions
  Troubleshooting HVAC control systems or changing HVAC filters provided workers are not exposed to rotating machinery.
  I&C controlled instrument valves under control of approved procedures or Work Orders.
  Instrument work where the process is isolated by a thermo well.
  Calibrating pressure, level, flow and temperature instruments.
  Work involving process sensor filling, venting, draining and sensing line blowdowns.
  Lifting leads for calibration and troubleshooting.
Notes: <number>
<number>
<number>
<number>

## Slide 25
<number>
SAFETY TAGGING
Unprotected Work :
Voltage checks and troubleshooting. (Reference MMA18).
Stroking of valve and actuator to determine proper operation.
Calibration, surveillance, and troubleshooting instrument loops (pneumatic/ electronic), including AC power and high voltage power supplies to the instruments.
System dynamic adjustments on plant instruments/equipment that require normal lineups.
Limit and torque switch adjustments conducted with approved procedures and using standard electrical safety precautions. (Reference MMA18).
Breaker maintenance while breakers are removed from the cubicle with no possibility of inadvertent reconnection (removed from cubicle).
Online packing gland adjustments on pumps and valves when authorized in an approved procedure or Work Order.
Greasing of rotating equipment.
Valve handwheel replacement.
Primary and Auxiliary systems chemistry sampling.
Notes: <number>
<number>
<number>
<number>

## Slide 26
<number>
SAFETY TAGGING
Unprotected Work :
Infra Red camera monitoring of equipment conditions.
Vibration testing on operating equipment.
Removing and installing limit switches which do not require leads to be de-termed when there is no mechanical hazard.
Removing and installing mechanical insulation.
Installing and removing scaffold when there is no adjacent hazard such as energized crane rails.
Notes: <number>
<number>
<number>
<number>

## Slide 27
<number>
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>

## Slide 28
<number>
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>

## Slide 29
<number>
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>

## Slide 30
<number>
SAFETY TAGGING
TERMINAL OBJECTIVE
Students will understand the need for and fundamentals of power plant safety tagging
Notes: <number>
<number>
<number>
<number>

## Slide 31
<number>
ENABLING OBJECTIVES
Describe the concept of hazardous energy sources .
Describe the process for establishing electrical protection boundaries.
Describe the process for establishing mechanical protection boundaries.
Describe the process to create a protection contract between workers and the operating authority
Students will be familiar with the procedure used to hang and verify safety tags
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>

## Slide 32
<number>
QUESTIONS ???????????
SAFETY TAGGING
Notes: <number>
<number>
<number>
<number>