## Slide 1
ACADs (08-006) Covered
Keywords
Cathodic protection, corrosion.
Description
Supporting Material
Cathodic Protection Systems
5.3.2.2 |  |  |  |  |  |  | 

## Slide 2: Cathodic Protection systems

## Slide 3
Title: Cathodic Protection System Number: AT-1060-LP-Cathodic Protection Revision: 0.0 Program: NET NLO Author: Alex Ramos Date: 4/26/2011
IT Review: Date: Approved: Date: Instructor Guidelines: Lesson Format PowerPoint Presentation Materials Computer Projector Evaluation Written exam in conjunction with other lesson plans, presentations, and handouts Remarks None References 1X4AB07-00014 CAPAC Instruction Manual

## Slide 4
Rev No | Date | Reason for Revision | Author’s Initials | Supv’s Initials
0.0 | 04/26/11 | Initial Development | AWR | 
 |  | ACAD item 5.3.2 |  | 

## Slide 5: Objectives: 1. Explain the purpose of the CATHODIC PROTECTION SYSTEM. 2. Discuss where CATHODIC PROTECTION SYSTEMS are applied. 3. Understand why corrosion is a concern to the plant systems. 4. Discuss the Components associated with a Cathodic Protection System. 5. Understand the range of operation for the system for different materials.

## Slide 6: What is CORROSION?
The word “corrosion” refers to the destruction of a metal or alloy by chemical or electro-chemical reaction with its environment.
The most common types:
- Electro-chemical corrosion
- Galvanic corrosion
Two basic requirements must exist : 1-anodic and cathodic areas must exist or have two dissimilar metals electrically joined. 2-Must be a path for current flow or metals immersed in an electrolyte (water)
Notes: Video of corrosion on top of simple 9v battery must click on picture for video to play this is time lapse but you get the ideal of what corrosion is and how quickly it can happen.

## Slide 7: Purpose
To eliminate the rusting or corrosion which occurs on metals immersed in water.
CAPAC
CAthodic Protection Automatically Controlled
Notes: Objective #1
The anode is the point where the current leaves the metal and CORROSION occurs. The cathode is the point where current reenters the metal and corrosion does not occur

## Slide 8: Applies to fixed structures such as:
1. Tanks
2. Condenser Water Boxes
3. Piers
4. Docks
5. Evaporators
6. Valves piping and other metal surfaces submerged in a liquids which support corrosion.
Notes: Objective #2

## Slide 9: System Components
1. Control Amplifier
2. Power Supplies
3. Reference Electrode
4. Anodes
5. Metal surface of material (CATHODE)
Notes: Objective #4

## Slide 10: Controller (Control Panel)
An amplifier which compares the level of cathodic protection of the metal as determined from the reference electrode with the desired level of protection as set by the operator. Amplifies the difference between two levels and sends an electrical signal to the power supply which controls the amount of current delivered to the anodes.

## Slide 11: Controller consist of
Control Amplifier- which is connected to the reference electrode, delivers a signal to one or more power supplies.
Power Supply- applies a potential across the anodes and metal to be protected. Converts AC power to low voltage high current DC and provides a means of adjusting the value of this DC over a wide range as set by controller.

## Slide 12: System Probes
Reference electrode – mounted next to the or through the metal surface to be protected. Made of a silver mesh screen coated with silver chloride.
Anodes- immersed in corrosion medium, mounted through walls of tank or water box or suspended from pier. Electrically insulated from metal cathode. Made of Platinum applied to a subsurface of titanium, niobium or tantalum.

## Slide 13: Two General types of protection with Cathodic protection systems
SACRIFICIAL ANODE
By the use of a metal which will suffer galvanic corrosion, such as Zinc, when zinc is electrically connected to steel, it has a higher potential and will act as the anode and emit current which passes into the steel. The steel is cathodically protected and the zinc will corrode, SACRIFICING itself for the protection of the steel.
IMPRESSED CURRENT
Places a voltage on a conductive material and forcing it to emit a current, which protects the steel. The material chosen (anode) has a high resistance to corrosion and is not destroyed such as platinum.

## Slide 14: System Operation
Notes: Walk through the basic operation of the system which based on the material will use current flows in the range of 0.4 to 1.3 voltage drop across materials.
A basic walkthrough the system and component operation can be acquired from the Cathodic Protection system Tech Manual (Which is located on the share point site) section 5.1.2 and sections 6 explain system operation and corrosion details.

## Slide 15: Examples of potential values for various types of materials
Notes: Objective #5 this is for understanding the system uses small values of voltage potential to accomplish the function of cathodic protection.

## Slide 16: Example of Impressed current
Notes: Video of impressed current system about 1:20 sec long Must be in presentation mode after screen shot comes up click once on screen and video will play.

## Slide 17: Objectives: 1. Explain the purpose of the CATHODIC PROTECTION SYSTEM. 2. Discuss where CATHODIC PROTECTION SYSTEMS are applied. 3. Understand why corrosion is a concern to the plant systems. 4. Discuss the Components associated with a Cathodic Protection System. 5. Understand the range of operation for the system for different materials.

## Slide 18: Questions?????