## Slide 1
ACADs (08-006) Covered
Keywords
  Governor Control, Starting Air, Fuel Oil and Storage, Lube Oil and Storage, Air Cooler Coolant, Jacket, Coolant, Air Intake and Exhaust, Diesel Generator, Service Water
Description
The purpose of this class is to familiarize students with EMERGENCY POWER SYSTEMS.
We will use various drawings of the EMERGENCY POWER SYSTEMS at Fermi 2 as the primary tools to learn this system.
Supporting Material
5.3.2.4 | 5.3.2.9 |  |  |  |  |  | 
Notes: <number>

## Slide 2
<number>
EMERGENCY POWER SYSTEM
TERMINAL OBJECTIVE
Students will understand the EMERGENCY POWER SYSTEMS, its major components and flowpaths
Notes: <number>
<number>
<number>
<number>

## Slide 3
<number>
EMERGENCY POWER SYSTEM
ENABLING OBJECTIVES
State the purpose of the EMERGENCY POWER system, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the EMERGENCY POWER system.
Identify the modes of operation of the EMERGENCY POWER system, including the major components associated with each mode.
Describe the basic interrelationships between the EMERGENCY POWER system and other plant systems.
Explain the basic principles of operation for the EMERGENCY POWER system and the major components and equipment.
Notes: <number>
<number>
<number>
<number>

## Slide 4
<number>
EMERGENCY POWER SYSTEM
Purposes of the EMERGENCY POWER (EAC) system
The purpose of the EDG is to provide a reliable on-site source of AC electrical power to maintain the ability to safely shutdown the reactor under all conditions, including a LOCA coincident with a Loss of Offsite Power (LOP)
Notes: <number>
<number>
<number>
<number>

## Slide 5
<number>
EMERGENCY POWER SYSTEM
Basic system description:
The EDGs start automatically upon receipt of LOCA and/or LOOP signal and reach rated speed and voltage within 10 seconds. However, the EDGs breakers will not automatically close to the plants electrical bus network unless either a LOOP and/or loss of EDG bus voltage occurs. If a LOOP and/or loss of EDG bus voltage occur an automatic sequencer will load the EDGs in an orderly manner to avoid overloading and damaging the equipment. Only the loads necessary for safe shutdown are automatically loaded to the EDG.
The system consists of four EDG units separated into two independent divisions. Each division containing two EDGs supplies power to the essential loads of its respective bus. Either divisional pair is capable of supplying loads needed for safe shutdown of the reactor. Each EDG is supplied with its own supporting systems such that any single failure of an EDG supporting system will not affect the remaining EDGs.
Notes: <number>
<number>
<number>
<number>

## Slide 6
<number>
EMERGENCY POWER SYSTEM
Basic system description:
Offsite power is the normal source of power to the ESF Electrical System. 120 kV AC from the Fermi 1 Mat supplies Div 1. 345 kV AC supplies div. 2. Each 4160 and 480V ESF arrangement is similar. Normal feed breaker is the "6" breaker. Power is fed to the EDG bus via the "8" breaker. Cross-divisional maintenance power is fed through the "9" breaker. The EDG can supply power to the ESF bus through the "3" breaker.
After a LOCA and on receipt of an automatic signal from the power plant relays, each unit automatically "fast starts", comes to rated voltage and synchronous speed, and is capable of operating as an isolated source to start loads sequentially. If a loss of system power has occurred, the EDG is automatically connected to the bus. If bus voltage is normal, the EDG idles at synchronous speed and rated voltage.
Notes: <number>
<number>
<number>
<number>

## Slide 7
<number>
EMERGENCY POWER SYSTEM
Basic system description:
If Offsite power is lost during parallel operation with the electrical system, the diesel output breaker will be opened automatically by under frequency relaying. This is the quickest method of tripping the EDG while it is maintaining the system loads.
The operation of the under frequency relay will open the EDG output breaker only when the EDG is paralleled with the Offsite system. Opening the EDG output breaker will cause an undervoltage condition on the affected bus. The breaker will reclose automatically as soon as all designated loads are removed from the bus.
Notes: <number>
<number>
<number>
<number>

## Slide 8
<number>
EMERGENCY POWER SYSTEM
Each EDG is completely independent from the other units, and has the following subsystems:
  Governor Control
  Starting Air
  Fuel Oil and Storage
  Lube Oil and Storage
  Air Cooler Coolant
  Jacket Coolant
  Air Intake and Exhaust
Diesel Generator Service Water
Notes: <number>
<number>
<number>
<number>

## Slide 9
<number>
EMERGENCY POWER SYSTEM
The EDGs are housed in a reinforced-concrete, Category I structure (RHR Complex).
Each unit is completely enclosed in its own concrete cell and is isolated from the other units. The building is designed to the following requirements:
  The building is protected against flood damage to elevation 590 ft
  The RHR complex structure is designed so that a turbine missile will not result in the failure of more than one system division
  The EDG system is designed to be operable during and after a design-basis tornado that has the following characteristics:
    External wind forces resulting from the tornado funnel, which have a horizontal peripheral velocity of 300 mph and a transient horizontal velocity of 60 mph
    Differential pressure between inside and outside of fully enclosed areas - 3 lb/in.2
Notes: <number>
<number>
<number>
<number>

## Slide 10
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 11
<number>
EMERGENCY POWER SYSTEM
EDG information:
Four Colt Industries Fairbanks-Morse 38TD8-1/8 diesels, rated at 3,967HP at 900 rpm, driving a 4160VAC, 3250kW salient pole generator, and attendant switchgear.
Diesel engine: 12 cylinder, opposed piston, dual crankshaft connected by a vertical drive (bevel gear). The crankshafts rotate in opposite directions. The lower crankshaft leads the upper by 18o. The lower crankshaft delivers power to the generator through the crankshaft coupling. A timing chain drives 2 camshafts from the upper crankshaft. The camshafts determine the timing of fuel injection.
The engines are capable of being started from a hot shutdown condition without outside auxiliary service, except 130VDC control power from divisional batteries. They reach rated voltage and synchronous speed (unloaded) within 10 sec after initiation of a starting signal.
Notes: <number>
<number>
<number>
<number>

## Slide 12
<number>
EMERGENCY POWER SYSTEM
EDG information:
Generator - Air cooled, 0.8 power factor, 4160VAC, 60 Hz, 3 phase, 8-pole, with a rating of 4063kVA. The generator and excitation system are designed using a solid-state excitation system and fast-response electrohydraulic governors so that, for sequential starting of ECCS motors, bus voltage will not dip below an acceptable limit.
Voltage is regulated automatically although the automatic voltage regulator setpoint may be varied. Voltage and speed control is provided locally and in the Main Control Room. Voltage regulation is maintained by controlling excitation current. The excitation current output determines the strength of the magnetic field, which controls voltage.
Initial excitation (field flashing) is automatically energized from a DC external power source when engine speed is at 250 rpm until generator voltage reaches 70% of rated when the field flash is deenergized.
Notes: <number>
<number>
<number>
<number>

## Slide 13
<number>
EMERGENCY POWER SYSTEM
EDG information:
The generator ratings are as follows:
  Continuous: 2,850kW
  2,000 hr: 3,100kW
  300 hr: 3,250kW
  30 minutes: 3,500kW
  Operation: When synchronizing an EDG to off site power, the frequency (speed) of the EDG must be higher that of the grid as indicated by the sychroscope rotating slowly in the fast direction. This is to help the EDG assume load when it is synchronized. More load must be applied immediately (about 300KW ) or the EDG will trip on reverse power. This is due to the relatively small generator being synchronized to the grid. Generator voltage must be slightly higher that grid voltage to assume some reactive load when synchronized.
Notes: <number>
<number>
<number>
<number>

## Slide 14
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 15
<number>
EMERGENCY POWER SYSTEM
EDG Auxiliaries information:
Fuel Oil and Storage –
Fuel Oil Storage Tanks store a 7 days fuel supply at 210 gal/hr, plus fuel required for routine engine testing. Each diesel generator has a 42,000 gallon diesel fuel storage tank located adjacent to the diesel generator. Each storage tank is fitted with level indicators and high and low level alarms. Redundant motor operated and manual valves for draining of the storage tank are provided. Fuel quality in the storage tanks is assured by using 2 strainers between the storage tank and the fill line connection and by performing delivery and periodic sampling for water, sediment, and other selected parameters.
Fuel Oil Day Tanks store sufficient fuel oil to supply the engine and motor-driven fuel oil pumps to support at least 1 hours of full load operation. Each has a capacity of 550 gallons, fitted with a level indicator and low-level alarm.
Notes: <number>
<number>
<number>
<number>

## Slide 16
<number>
EMERGENCY POWER SYSTEM
EDG Auxiliaries information:
Fuel Oil and Storage –
Fuel Oil Transfer Pumps pump fuel oil from the storage tanks to the day tank. They are rotary gear pumps, 10 gpm/pump capacity, driven by 1HP motors. They are controlled from Main Control Room panel P809 or P810 in conjunction with switches located on the local EDG Control panel.
Engine-Driven Fuel Oil Pumps supply the diesel injectors with fuel oil drawn from the day tank through a strainer. One pump per diesel, driven from the engine governor drive. Pump discharges 9 gpm at 35 psig through a duplex fuel oil filter.
Notes: <number>
<number>
<number>
<number>

## Slide 17
<number>
EMERGENCY POWER SYSTEM
EDG Auxiliaries information:
Diesel Generator Service Water –
DGSW removes heat from Air Cooler Coolant, Lube Oil and Jacket Coolant subsystems. Each DGSW pump takes a suction on the RHR reservoir and discharges through a check valve that prevents reverse flow, a normally open manual valve, and through a flow element to the EDG skid.
A discharge pressure control valve inboard of the discharge check valve limits DGSW pressure by bypassing water to the RHR reservoir, if needed. A throttle valve is provided before the coolers to adjust flow. Normal flow through the engine coolers is approximately 920 to 940 gpm.
The service water passes through the air cooler, lube oil cooler and jacket cooler, out a manual isolation valve, then to the mechanical draft cooling towers through motor operated valves. The water is cooled and returned to the RHR reservoir.
Notes: <number>
<number>
<number>
<number>

## Slide 18
<number>
EMERGENCY POWER SYSTEM
EDG Service Water system
Notes: <number>
<number>
<number>
<number>

## Slide 19
<number>
EMERGENCY POWER SYSTEM
EDG SW Pump Logic
Notes: <number>
<number>
<number>
<number>

## Slide 20
<number>
EMERGENCY POWER SYSTEM
EDG Auxiliaries information:
Diesel Generator Service Water –
DGSW Pumps: 2 stage, vertical turbine type with service water-cooled bearings. There is 1 pump per diesel, with a capacity in excess of 950 gpm. The pump is driven by a 50HP, 480VAC motor.
Automatically starts after the EDG starts.
DGSW Pumps have Minimum Flow Recirc Valves to protect the pump from damage caused by pumping against a shutoff head. The valve opens when system pressure is 57 psig.
DGSW Heat Exchangers remove heat from Air Coolant, Lube Oil, and Jacket Coolant subsystems.
Jacket Coolant - During diesel operation, the engine-driven Jacket Coolant Pump takes a suction on the Jacket Coolant Heat Exchanger. The pump discharges into the engine and turbocharger water jackets.
The coolant passes through a temperature control valve to either flow through the jacket coolant heat exchanger or bypass the heat exchanger back to the pump suction for re-use.
Notes: <number>
<number>
<number>
<number>

## Slide 21
<number>
EMERGENCY POWER SYSTEM
EDG Jacket Cooling Water system
Notes: <number>
<number>
<number>
<number>

## Slide 22
<number>
EMERGENCY POWER SYSTEM
EDG Lube Oil system
Notes: <number>
<number>
<number>
<number>

## Slide 23
<number>
EMERGENCY POWER SYSTEM
EDG Room Ventilation system
Notes: <number>
<number>
<number>
<number>

## Slide 24
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 25
<number>
EMERGENCY POWER SYSTEM
EDG Fuel Oil
System
Notes: <number>
<number>
<number>
<number>

## Slide 26
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 27
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 28
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 29
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 30
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 31
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 32
<number>
EMERGENCY POWER SYSTEM
Notes: <number>
<number>
<number>
<number>

## Slide 33
<number>
EMERGENCY POWER SYSTEM
EDG Auxiliaries information:
Starting Air –
Provides pressurized air from the air receivers to turn the engine over, and to supply control air to the Air Cooler Coolant Temperature Control System. Additionally, the air system provides air to the main bearing oil boosters and the governor booster during EDG starts.
On receipt of a start signal, air flows through both air start solenoid valves, to the air start headers and distributors. Air sent through the distributors opens air start check valves in cylinder firing order. This allows air from the air headers to enter the cylinders, pushing the pistons apart, causing the engine to rotate.
If the starting air compressor for one EDG becomes unavailable the starting air system can be cross connected with the other EDG starting air system in the same division.
Notes: <number>
<number>
<number>
<number>

## Slide 34
<number>
EMERGENCY POWER SYSTEM
Importance of the EAC system to nuclear safety:
The EAC system is possibly the most vital system at any nuclear power plant. The major focus of original nuclear design was being able to mitigate a LOCA and the ECCS systems were of paramount importance. In the last 15 years there has been a major change in nuclear power safety philosophy. Actual operating experience has shown that Loss of Offsite Power (LOP) has a fairly high likelihood of occurrence, whereas probability of a major LOCA remains very small. LOP scenarios can lead to core damage because ECCS systems rely on AC power.
The Fukasheima disaster has certainly established further proof of the need to focus heavily on the reliability and durability of EAC systems
Notes: <number>
<number>
<number>
<number>

## Slide 35
<number>
EMERGENCY POWER SYSTEM
TERMINAL OBJECTIVE
Students will understand the EMERGENCY POWER SYSTEMS, its major components and flowpaths
REVIEW
Notes: <number>
<number>
<number>
<number>

## Slide 36
<number>
EMERGENCY POWER SYSTEM
ENABLING OBJECTIVES
State the purpose of the EMERGENCY POWER SYSTEM, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the EMERGENCY POWER SYSTEM.
Identify the modes of operation of the EMERGENCY POWER SYSTEM, including the major components associated with each mode.
Describe the basic interrelationships between the EMERGENCY POWER SYSTEM and other plant systems.
Explain the basic principles of operation for the EAC system and the major components and equipment.
REVIEW
Notes: <number>
<number>
<number>
<number>