## Slide 1
ACADs (08-006) Covered
Keywords
Starting current, running current, motor failure indications, circulating water pump, condensate pump, centrifugal pump, overloading, rotor, bearings, pump law relationship, starting resistance.
Description
Supporting Material
Plant Overview--Motors
1.3.5.2 | 2.1.14.4 | 5.1.1.2.1.12a | 5.3.2.3 | 5.3.2.9 |  |  | 

## Slide 2: Plant Overview Motors

## Slide 3
Title: Plant Overview Motors Number: AT-1060-LP-Plant Overview Motors Revision: 0.0 Program: NET NLO Author: Alex Ramos Date: 5/01/2011
IT Review: Date: Approved: Date: Instructor Guidelines: Lesson Format PowerPoint Presentation Materials Computer Projector Evaluation Written exam in conjunction with other lesson plans, presentations, and handouts Remarks None References DOE AC & DC Motors , NRC Generic Fundamentals

## Slide 4
Rev No | Date | Reason for Revision | Author’s Initials | Supv’s Initials
0.0 | 05/02/11 | Initial Development | AWR | 
 |  | This lecture is designed to cover and build upon ACAD sections 2.1.5 Failure Indications Motors, 5.1.1.2 motors and 5.3.2 systems with large motors and their characteristics. |  | 

## Slide 5: Objectives
Discuss why starting current is an important factor when starting an AC or DC motor.
Explain how starting current is limited in DC motors.
Review limitations associated with AC motor starts.
Discuss motor failure indications.
Show how to apply the basic pump laws to motor calculations.
Notes: Voltage 1&2 unit component pictures are used plant 3 and 4 will have similar components in place.

## Slide 6: Circ Water Pump Motor
Notes: This slide is to show the size and scale of some motors on site very large, therefore starting currents and surges will be more pronounced with these motors.

## Slide 7: Vertical Centrifugal Pumps
The Pump shaft is vertical and positioned above the Pump.
MOTOR
CIRCULATING
WATER
PUMPS
Notes: Pumps are submerged in the water. Two Circulating Water pumps supply the driving head for Circulating Water through the System. Each Circulating Water pump is a vertical, single stage, open impeller Unit. The two pumps are located at the end of the Cooling Tower flume in a 35 ft deep pit to achieve the required NPSH. The pump discharge is approximately at ground level and the impeller near the bottom of the pit. The pumps are rated at 242,300 gpm each at a discharge pressure of 41 psig

## Slide 8
RHR Pump

## Slide 9: Vertical Centrifugal Pumps
RHR Pump
400 HP
3788 GPM
MOTOR
PUMP

## Slide 10: Condensate Pumps

## Slide 11: Vertical Centrifugal Pumps
Reactor Coolant Pumps
100,600 gpm
MOTOR
PUMP

## Slide 12: Starting Current
Starting current in AC motor is greater than normal running current drawn by motor
There are three reasons for increased current:
  Power required to initially build up rotating magnetic field in stator
  Extra energy required to overcome inertia of rotor in order to place it in motion
  Interactions occur between rotor currents and stator’s magnetic field, resulting in high currents being drawn by motor
Notes: Objective #1

## Slide 13: Starting Current
Instant motor first started, rotating magnetic field is produced in stator
  Rotor not yet rotating
Stator experiences a large current draw initially to establish rotating magnetic field
  Very little resistance to current flow in stator initially
Notes: Basic operation of an induction motor.

## Slide 14: Starting Current
Rotating magnetic field from stator cuts conductors in rotor resulting in EMF induced in rotor
Rotor’s conductors shorted to one another, causing current flow and resulting magnetic field around rotor
Notes: Basic operation of an induction motor.

## Slide 15: Starting Current
As soon as the magnetic field is established in the rotor
  The rotor’s magnetic field cuts the conductors within the stator
  Causing a voltage to be produced within the stator
This induced voltage opposes the applied voltage within the stator field
  Referred to as counter electro-motive force (CEMF)
  CEMF acts to limit current within the stator field during motor operation
Notes: 15
This is how CEMF limits Ia

## Slide 16: Starting Current
Starting current typically 5 to 7 times amount of motor full load current
  Motor full load current is amount of current that motor will draw from power source when motor is being used at full capacity
Full load current for motor is always shown on motor’s nameplate data (ratings)
Notes: Objective #1 , 5 to 7 times the normal running current value is typical on most motors.

## Slide 17: Starting Current
Starting current can be observed on (current meters) when large motors are started.
In many cases ammeter’s needle will “peg high” on motor start, then drop down to normal operating current value as the system is started.
  Normal indications are observed
If starting current is not observed ⇒this is an abnormal indication which requires investigation
Notes: The starting current can be observed on the power supply instrumentation of the turbine or diesel generator supplying the load.

## Slide 18: Starting Current
Large starting current surges in AC motors result in additional heat being produced in motors’ stators and rotors
In order to prevent damage to large AC motors from excessive start attempts, number of successive starts is usually limited, based on time between starts

## Slide 19: Starting Current
Starting attempts for large AC motor may be limited to 4 per hour, or 1 start attempt every 15 minutes
  Limits may be imposed procedurally or by design of motor’s control circuitry
Limiting number of successive starts on large AC motor allows motor to dissipate heat created by large starting currents
  Prevents damage to motor’s stator and rotor conductors
Notes: Objective #3
Minimizing the Effects of Starting Current
Some motor starting circuits are equipped with interlocks which: Limit number of successive motor start attempts OR Ensure minimum time elapsed between successive start attempts To prevent damage to the motor from high starting current

## Slide 20: Starting Current
Minimizing the Effects of Starting Current
  Start motor unloaded to quickly establish stator counter electromotive force (CEMF)
    Requires shorter time for motor to reach stable running current
  Some large motors equipped with special starting circuits designed to limit current during motor start
    For example, a three phase AC motor can be started with its windings in a wye config to minimize starting current
      Once operating speed is reached, the windings can be switched to delta config for greater power .

## Slide 21: Running Current
Once an AC motor is started, the amount of current it draws while running is directly proportional to the load placed on the motor.
  Increased loading results in increased current draw
Abnormally high running currents should be investigated
  May indicate problems such as mechanical binding within the motor, or load being driven by motor (pump, valve lineups, flow blockage, etc.)

## Slide 22: Motor Overloading
  High operating current could result from:
    Gradual bearing failure
    Locked or seized rotor (shaft) of the motor or the load (pump, valve, etc.)
    Under voltage condition (P = EI)
  Increased current flow could be high enough to cause:
    Thermal overload trip resulting from increased temperature
    Trip of the supply circuit breaker
Notes: Objective #4

## Slide 23: Motor Overloading of MOV’s
  Motor overload can also occur when packing on a motor-operated valve (MOV) is tightened excessively
    Motor current would increase, due to the increased torque the motor would have to produce to overcome the additional friction associated with the packing
    These high operating currents can result in excessive heat being generated within the motor, causing break down of the motor winding insulation and damage to the motor
Notes: Objective #4, One of the most common problems noted with motor operated valves (MOV) maintenance.

## Slide 24: Abnormal Motor Indication
Abnormally low or no running current as indicated on an amp meter should be investigated as this may indicate a problem such as a sheared shaft, rotor malfunction or coupling failure.
Notes: Objective #4

## Slide 25: Loss of Motor Cooling
Continuous operation of a motor at rated load with a loss of required cooling to the motor windings will eventually result in breakdown of the motor insulation due to overheating
  Causing increased current flow due to a decrease in resistance (short circuit)
Notes: Objective #4

## Slide 26: Component Mechanical Problems
Loads driven by electrical motors (pumps, blowers, fans, etc.) may experience mechanical problems such as:
  Locked (seized) rotor
  Binding or rubbing of impeller/fan blades
  Sheared rotor
  Failed bearings
Notes: 26
Objective #4

## Slide 27: Component Mechanical Problems
Locked (Seized) Rotor
Results from the driven mechanical component causing the motor rotor not to turn. Which results in a locked shaft of the motor rotor (shaft) and possible failure of associated or component bearings.
Notes: 27

## Slide 28: Component Mechanical Problems
Locked (Seized) Rotor
Indications of a locked rotor:
  Tripping of component circuit breaker
  Immediate reduction in system flow rate
  Immediate reduction in component discharge pressure
  Immediate rise in component current to supply the needed torque
  Immediate rise in motor winding temperatures resulting from greater current flow
Notes: 28
These are some of the most common indications , these are also indications used for binding/rubbing of shaft impeller/fan. Note the most noticeable indication will be increased noise or abnormal noise levels. Vibration levels will also rise with the component and lead to possible alarms and warnings from installed monitoring/troubleshooting systems.

## Slide 29: Component Mechanical Problems
Sheared Rotor
Motor becomes separated from mechanical portion of pump (shaft/coupling breaks)
Motor operates freely (spinning) with no load mechanically attached
Notes: 29
Motor has power available and is turning, however no work is being done by the motor.

## Slide 30: Component Mechanical Problems
Sheared Rotor
Indications of sheared rotor:
  Load has no (low) running current (as indicated on amp meter)
  Immediate reduction in system flow rate
  Immediate reduction in component discharge pressure
Notes: 30

## Slide 31: Component Mechanical Problems
Failed Bearings
Bearing failure can result from a number of circumstances:
  Insufficient lubrication
  Poor bearing maintenance practices
  Improper loading of the component
  Motor under-voltage operations (P=EI if (E) lowers will cause (I) to raise for constant Power. This higher (I) can breakdown bearing insulation, which can lead to damage)
  Any condition leading to overheating of the bearings can cause bearing failure
Notes: 31

## Slide 32: Electric Motor Pump Laws Relationships
These laws establish the following:
  Flow rate is directly proportional to pump speed
  Discharge head is directly proportional to the square of pump speed
  Power required by the pump motor is directly proportional to the cube of pump speed
  V  N HP  N2 P  N3 I  N3
Notes: Pump laws were covered in detail during NUET 1150, this is just a quick review to look at the application of the laws with speed, current and power.

## Slide 33: Electric Motor Pump Laws Relationships
  V  N HP  N2 P  N3 I  N3
  Where:
    V = volumetric flow rate of pump (gpm or ft3/hr)
    N = speed of pump impeller (rpm)
    Hp = head developed by pump (psid or feet)
    P = pump power (kW)
    I = pump motor current (amperes)
Notes: Review of the major terms

## Slide 34: Pump Laws #1:
Since we know the volumetric flow rate (capacity) is directly proportional to the pump speed, we can write the following equation relating the conditions at one speed to those of another:

## Slide 35
Pump Laws #2:
Pump head is directly proportional to the square of the pump speed,

## Slide 36
Pump Laws #3:
Pump power is directly proportional to the cube of the pump speed,

## Slide 37: Review Question
A centrifugal pump is operating with the following parameters:
  Pump speed = 1,800 rpm
  Pump head = 100 psid
  Motor current = 10 amps
What will be the new value of pump head if the speed is increased such that the current requirements are now 640 amps?
  A. 400 psid
  B. 800 psid
  C. 1,200 psid
  D. 1,600 psid
ANSWER: D
Notes: Objective #5

## Slide 38: Solution

## Slide 39: Starting DC Motors - Starting Current
At moment DC motor is started rotor (armature) is stationary and there is no counter EMF being generated
Only component available to limit starting current is resistance of armature, which is really nothing more than length of copper wire

## Slide 40: Starting DC Motors - Starting Current
In most DC motors this is a very low value ≈ 1 ohm or less

## Slide 41: Starting DC Motors - Starting Current
In order to reduce very high starting current, an external resistance must be placed in series with armature during starting period
Consider a 10-hp motor with an armature resistance of 0.4 ohms
If motor were supplied by 260 VDC, resulting current would be as shown
Notes: Three additional mouse clicks to reveal entire slide contents.

## Slide 42: Starting DC Motors - Starting Current
Large starting current is approximately twelve times greater than actual full-load current for this motor
  High current would, in all probability, cause severe damage to brushes, commutator, or windings
Starting resistors are usually incorporated into motor design to limit starting current to 125 to 200 percent of full load current
Notes: Objective#1 , Two additional mouse clicks to reveal entire slide contents.

## Slide 43: Starting Resistance
Amount of starting resistance necessary to limit starting current to more desirable value can be calculated
Rs = starting resistance
Et = terminal voltage
Is = desired armature starting current
Ra = armature resistance
Notes: Three mouse clicks to reveal entire slide contents.

## Slide 44: Starting Resistance Example
If the full load current of the motor mentioned previously is 50 amps, and it is desired to limit starting current to 125% of this value, find the required resistance that must be added in series with the armature.
Notes: This value for starting resistance (Rs) is then added to the Ra (Ra + Rs) to limit the starting current of the motor during the startup procedure. One additional mouse click to reveal entire slide contents.

## Slide 45: Starting Resistance
Starting resistors are normally placed in circuitry of motor controller that is used to start motor
Variable resistors are normally used as starting resistors for DC motors
  Allows value of resistance in starting circuit to be manually or automatically controlled as motor is started
Maximum amount of resistance will always be inserted in starting circuit when motor is first started, since no CEMF exists in armature
Notes: Two additional mouse clicks to reveal entire slide contents.

## Slide 46: Starting Resistance
As speed of motor increases, CEMF will begin to increase, limiting armature current
Starting resistors are then “cut out”, in successive steps, until motor reaches full running speed and starting resistors are completely removed from circuit
When running at full speed, CEMF limits armature current and starting resistors are no longer necessary
Notes: Two additional mouse clicks to reveal entire slide contents.

## Slide 47: Review Question
The average starting current for an ac motor is approximately...
  A. the same as its normal running current.
  B. two to three times its normal running current.
  C. five to seven times its normal running current.
  D. ten to fifteen times its normal running current.
ANSWER: C.

## Slide 48: Objectives
Discuss why starting current is an important factor when starting an AC or DC motor.
Explain how starting current is limited in DC motors.
Review limitations associated with AC motor starts.
Discuss motor failure indications.
Show how to apply the basic pump laws to motor calculations.