## Slide 1
ACADs (08-006) Covered
Keywords
Defense-in-depth, reactor protection system, solid state protection system, reactor trips, Engineered Safety Feature System (ESFAS), Containment Cooling
Description
Supporting Material
Reactor Protection System
1.1.8.4.7 | 1.1.9.1.3 | 1.1.9.1.4 | 5.3.2.7 | 5.4.3.8 | 5.4.3.11 |  | 

## Slide 2: Reactor Protection System
Number: AT-1300-PP-RPS Rev: 1
Author: Rob Thomas Date: 6/28/11
Approved: Date:
References:
1 AT-1300-LP-RPS
2 V-LO-TX-28101 Reactor Protection System
VOGTLE ELECTRIC GENERATING PLANT

## Slide 3
Rev No | Date | Reason for Revision | Author’s Initials | Supv’s Initials

## Slide 4: OBJECTIVES
State the overall purpose of the Reactor Protection System (RPS).
Describe the defense-in-depth features of the RPS.
List three main functions of the Solid State Protection System (SSPS).
Describe the signals that provide inputs to the SSPS.
Describe how the SSPS is designed to satisfy the regulatory requirements for redundancy, independence, and testability.

## Slide 5: OBJECTIVES
Define the term coincidence-logic.
State the functions of the three major sections of the SSPS cabinet.
Describe the actions that occur to trip the reactor once the coincidence logic is met.

## Slide 6: Purpose:
Reactor Protection System is designed to guarantee the integrity of the 3 fission product barriers.
Which reduces the risk to the public during at-power operation and during accident conditions.

## Slide 7: Defense-In-Depth
The plant is designed to provide defense-in-depth to prevent the release of fission products to the environment.
Reactor Trips
Engineered Safety Feature System (ESFAS)
Containment Cooling

## Slide 8: Reactor Trip
aka Reactor Scram
First level of automatic protection
Inserts all of the control rods, which stops the fission process. Once the fission process has been stopped, heat generation from fission stops.
However, the core continues to generate heat from the decay of fission products.

## Slide 9: Engineered Safety Feature System (ESFAS)
A safeguards actuation is the next level of defense-in-depth protection.
ESFAS is designed to remove decay heat which could cause serious core damage and the subsequent release of fission products.
Safeguards actuation protects the fuel cladding and the Reactor Coolant System.

## Slide 10: Containment Cooling
Last level of automatic defense-in-depth protection.
Protects the Containment structure from over pressurization.
  Containment Spray System inside containment
  AP1000 uses a passive containment cooling system outside of containment.
This over pressurization of containment can be caused by a loss of coolant accident (LOCA) or by a loss-of-secondary coolant accident.

## Slide 11: Reactor Protection System

## Slide 12
Simplified Protection Circuit
Notes: An instrument loop consists of a transmitter or sensor for measuring a parameter, a power supply, a receiver and connecting cabling. For the sake of discussion we will use Pressurizer level channel I for an example. Transmitter LT-459 measures pressurizer level by the use of a D/P type sensor. Its loop power supply comes from NSSS protection cabinet I. A current signal of 4-20 mA is generated based on the level measured in the pressurizer. A constant voltage is sent to the transmitter via its loop power supply card. The resistance inside the transmitter is based on the level. This resistance changes the current signal from 4–20 mA. A signal converter changes this current signal to a 0-10 VDC signal. This 0-10 VDC signal is sent through isolated and un-isolated circuits. The isolated signal is sent to control board meters and alarms; NSSS control cabinet 2, and the integrated plant computer. One of the un-isolated signals is sent for reactor protection to an electronic on/off switch called a bi-stable. A bi-stable is a circuit that basically turns on or off its output based on a set point. Think of it as an electronic light switch. Example: In this case the “Pressurizer High Level Trip” set point is at 92%. When the bi-stable’s input reaches a voltage level for 92% level (approx. 9.2 VDC), its output automatically turns off. The output of the bi-stable interfaces SSPS by an input relay. The SSPS input relay for level channel 459 which is located in the channel I input bay (shown like the one below) is normally energized when level is below the trip set point. When the trip set point is exceeded, the input relay will lose its input signal form its bi-stable. SSPS will process this signal through its logic bay and if the coincidence and the permissive are met a reactor trip will occur. Some times it is necessary to remove an instrument channel from service due either maintenance or an action statement from the Technical Specification due to the failure of the channel to meet the Limited Condition for Operation (LCO). To place a channel in the trip condition all the bi-stables associated with channel must be tripped. This is performed by placing the associated bi-stables in the test position. The test relay removes the bi-stables output form the associated SSPS input relay. This action places the channel in the tripped condition.

## Slide 13
PT-455
NSSS PROTECTION CABINET CHANNEL 1
NSSS CONTROL CABINET
iso
iso
I
II
III
IV
I
II
III
IV
SSPS TRAIN A
SSPS TRAIN B
PI-455
iso
IPC
iso
PORV 455
Przr Heaters and Sprays
Notes: This diagram shows how instrumentation is monitored for protection and control. Pressure Transmitter 455 (PT-455) is used in the example.
Nuclear Steam Supply System (NSSS) Protection Cabinets provide the interface between safety related field inputs and SSPS and/or NSSS Control cabinets. Point out the signal flow path from the field transmitter to the NSSS Protection cabinets and distributed to the control cabinets for plant control, indicators for monitoring, and SSPS for reactor protection.

## Slide 14: Main Functions
Solid State Protection System (SSPS) receives various inputs and provides the following functions:
Generates Reactor trips
Generates safeguards actuations
  Places plant in safe condition by operating various plant components
Provides indication
  MCB trip-status lamps
  Control room annunciator panel
Notes: MCB= Main Control Board

## Slide 15: SSPS Input Signals
Process Instruments
  Bi-stable inputs from plant parameters: Press, Temp, Level, Flow
Nuclear Instruments
  Bi-stable inputs from nuclear power levels generated from reactor excore detectors
Field equipment
  valve position, breaker position
Main control board (MCB)
  manual switches, pushbuttons, etc

## Slide 16: RPS Design Regulations
10CFR50, Appendix A - states design criteria for protection system at nuclear plants.
Criteria include:
  Redundancy
  Independence
  Testability

## Slide 17: RPS Design Criteria
Redundancy
Two trains of protection, A and B
Multiple channels sensing same parameter
Individual channels feed both trains of SSPS
Single failure cannot cause loss of protection
  Coincidence-logic - specific number of multiple channels must indicate tripped in order to generate reactor trip or safeguard functions

## Slide 18: RPS Design Criteria
Independence
Channels measuring parameters must be physically and electrically separated (isolated)
Some protection channels may be used for automatic control systems (e.g., pressurizer level control)
Protection signals must be isolated from control/indication signals even though sensed by same detector (RTD, D/P cell, etc.)

## Slide 19: RPS Design Criteria
Testability
Must be able to test or calibrate channels without losing or causing protection function.
A channel failing while another channel in test (tripped) will cause a reactor trip function.
Dual-train design allows testing of one SSPS train while other provides protection.
Bypass breakers - one breaker in parallel with each reactor trip breaker

## Slide 20: SSPS Cabinet Major Sections
Input Relay Bay  input relays controlled by bistables
Logic Bay  performs coincidence logic conditions
Output Relay Bay  receives logic signals to control master & slave relays to control plant equipment
1
1
3
2
2
3

## Slide 21: SSPS Cabinet
Input Relay Bay
Acts as an isolation device between the various plant inputs and SSPS.
Divided into 4 compartments to provide separation between each input channel.
Each SSPS input relay bay is supplied from its respective channel 120 VAC power source.

## Slide 22
Simplified Protection Circuit
SSPS Input Relay Bay
Notes: An instrument loop consists of a transmitter or sensor for measuring a parameter, a power supply, a receiver and connecting cabling. For the sake of discussion we will use Pressurizer level channel I for an example. Transmitter LT-459 measures pressurizer level by the use of a D/P type sensor. Its loop power supply comes from NSSS protection cabinet I. A current signal of 4-20 mA is generated based on the level measured in the pressurizer. A constant voltage is sent to the transmitter via its loop power supply card. The resistance inside the transmitter is based on the level. This resistance changes the current signal from 4–20 mA. A signal converter changes this current signal to a 0-10 VDC signal. This 0-10 VDC signal is sent through isolated and un-isolated circuits. The isolated signal is sent to control board meters and alarms; NSSS control cabinet 2, and the integrated plant computer. One of the un-isolated signals is sent for reactor protection to an electronic on/off switch called a bi-stable. A bi-stable is a circuit that basically turns on or off its output based on a set point. Think of it as an electronic light switch. Example: In this case the “Pressurizer High Level Trip” set point is at 92%. When the bi-stable’s input reaches a voltage level for 92% level (approx. 9.2 VDC), its output automatically turns off. The output of the bi-stable interfaces SSPS by an input relay. The SSPS input relay for level channel 459 which is located in the channel I input bay is normally energized when level is below the trip set point. When the trip set point is exceeded, the input relay will lose its input signal form its bi-stable. SSPS will process this signal through its logic bay and if the coincidence and the permissive are met a reactor trip will occur. Some times it is necessary to remove an instrument channel from service due either maintenance or an action statement from the Technical Specification due to the failure of the channel to meet the Limited Condition for Operation (LCO). To place a channel in the trip condition all the bi-stables associated with channel must be tripped. This is performed by placing the associated bi-stables in the test position. The test relay removes the bi-stables output form the associated SSPS input relay. This action places the channel in the tripped condition.

## Slide 23: SSPS Cabinet
Logic Bay
Receives output from the input relay bays and from actuation and reset switches on the MCB
Performs coincidence - logic decisions (2/4, 2/3, etc.)

## Slide 24: SSPS Cabinet
Logic Bay
Generates Reactor Trip and Safeguards actuation signal.
  Reactor Trip action:
    Removes power to undervoltage (UV) coil of reactor trip breaker
    Reactor trip breaker opens to deenergize CRDMs
  Safeguards action controls master and slave relays in two output relay bays

## Slide 25
SSPS LOGIC BAY
Notes: Logic Bay
a. Receives Input from the input relays and directly from MCB switches to determine if the required logic for a reactor trip/safeguards actuation has been satisfied.
b. Logic Cards
(1) If the number of tripped inputs is greater than or equal to the required coincidence the logic card will generate an output.
(2) The output of some logic cards may be blocked by positioning MCB handswitch to block after the required permissives have been satisfied. Once established the block will remain active until the handswitch is taken to reset or the associated permissive signal is lost.
c.Driver Cards
(1) Once an output is received from a logic card a safeguards driver and/or the UV driver will cause component actuation.
(2) For reactor trip logic the UV driver will remove 43V DC from the RTBs & BYBs.
(3) For ESFAS logic the safeguards driver will apply 48V DC to a master relay which will in turn apply 120V AC to the slave relay resulting in component actuation.

## Slide 26
M/G Set
M/G Set
M/G Set Output Breaker
M/G Set Output Breaker
Reactor Trip Breaker “A”
Reactor Trip Breaker “B”
Reactor Trip Bypass Breaker “A”
Reactor Trip Bypass Breaker “B”
Rod Control Cabinets
Notes: Using this one line diagram introduce the students of how the reactor trip breakers fit in the reactor protection scheme. Point out the bypass reactor trip breakers and their purpose.
The rod control system requires power not only to move the control rods, but also to maintain their position. Each reactor trip breaker is controlled by its associated train of SSPS for reactor protection. When reactor protection is required, power is interrupted to the rod control system by the opening of the reactor trip breakers. This loss of power to the rod control system causes the control rods to drop into the core causing the reactor to shutdown.
Bypass Reactor Trip Breaker (BYB) is used to allow testing of its associated RTB while the plant is operating. The BYB is normally open and racked out to the disconnect position.

## Slide 27: SSPS Cabinet
Output Relay Bay
Safeguards signal from logic bay energizes master relay.
Master relay contact closes to energize slave relay(s).
Slave relay contact(s) operate to control various plant components (pumps, valves, etc.)

## Slide 28
R
MASTER
RELAYS
RELAYS
15 VDC
MODE
SELECTOR
SWITCH
TEST
OPERATE
P-11 & P-12
SIGNAL
48VDC
48VDC
15VDC
15VDC
SAFEGUARDS
DRIVER CARD
UNDERVOLTAGE
DRIVER CARD
ENABLE
CS TEST
PANEL
R
R
R
R
AY1A
(BY1B)
LOGIC CARDS
LOGIC TESTER
MULTIPLEXER
48 VDC
G
PERMISSIVES,
MEMORIES, &
BLOCKS
CHECK FOR PROPER
COINCIDENCE
SLAVE
Notes: a. Output Relay Bay #1 contains:
(1) Master relays
(2) Slave relays (protection)
(3) Output relay test panel
b. Output Relay Bay #2 contains:
(1) Slave relays only
(2) Relays in the upper section are control type relays,
relays in the bottom are protection only type relays.
c. Master Relays
(1) Each master relay can control up to 4 slave relays.
(2) The master relays are DC relays which energize to actuate (supplied with auctioneered 48 vdc from the Logic Bay).
(3) Relays are energized either by a driver card or directly by using the QMCB HS
d. Slave Relays
(1) Send the actual start/stop signals to various plant equipment.
(2) The slave relays are AC relays (120 vac) which energize to actuate.
(3) Many slave relays are arranged with a dual operating coil one which must energize to actuate the associated relay (latch coil) and one that resets the slave relay after it has been actuated (unlatch coil).
(a) Latching coil energizes when the associated master relay energizes.
(b) After the latching coil is de-energized the associated slave relay remains in the actuated position (similar to the operation of a lockout relay).
(c) To reset the slave relay to the normal alignment the unlatch coil must be energized by the operator (reset switch). 120 VAC power is required to energize the unlatch coil just as it is to energize the latching coil.
(d) If the latching coil is still energized and the associated unlatch coil is energized concurrently, the slave relay remains in the actuated position.

## Slide 29: Objectives Review
State the overall purpose of the Reactor Protection System (RPS).
Describe the defense-in-depth features of the RPS.
List three main functions of the Solid State Protection System (SSPS).
Describe the protection scheme that provides inputs to the SSPS.
Describe how the SSPS is designed to satisfy the regulatory requirements for redundancy, independence, and testability.

## Slide 30: Objectives Review
Define the term coincidence-logic.
State the function(s) of the three major sections of the SSPS cabinet.
Describe the actions that occur to trip the reactor once the coincidence logic is met.