## Slide 1
ACADs (08-006) Covered
Keywords
Containment Isolation, actuation logic,
Description
Supporting Material
1.2.1.5 | 3.3.2.4.2 | 4.10.4.2 | 5.3.2.7 | 5.4.3.11 |  |  | 
Notes: <number>

## Slide 2
<number>
CONTAINMENT
Notes: <number>
<number>
<number>

## Slide 3
<number>
Students will understand the CONTAINMENT ISOLATION system, actuation logic and its major components
TERMINAL OBJECTIVE
Notes: <number>
<number>
<number>

## Slide 4
<number>
ENABLING OBJECTIVES
State the purpose of the CONT system, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the CONT system.
Identify the modes of actuation of the CONT system, including the major component groups associated with each mode.
Describe the basic interrelationships between the CONT system and other plant systems.
CONTAINMENT (CONT)
Notes: <number>
<number>
<number>

## Slide 5
CONTAINMENT (CONT)
<number>
Purposes of the CONTAINMENT (CONT) system
Provide an essentially leak-tight barrier against the uncontrolled release of radioactivity to the environment, and to assure that the containment design conditions important to safety are not exceeded for as long as postulated accident conditions require.
Notes: <number>
<number>
<number>

## Slide 6
<number>
CONTAINMENT (CONT)
PRIMARY
CONTAINMENT
Notes: <number>
<number>
<number>

## Slide 7
MCCC - NUET 130

## Slide 8
<number>
CONTAINMENT (CONT)
Notes: <number>
<number>
<number>

## Slide 9
CONTAINMENT (CONT)
<number>
Safety Design Basis of the CONT system
Shall ensure sufficient boron injected at a flowrate of at least 41.2 gallons per minute to bring the Reactor from full power to cold, Xenon-free shutdown condition. Control rods are assumed to remain in 100% rated power pattern
In the event of a LOCA resulting in core damage, the operators will inject CONT to control pH in the Suppression Pool. Since there is limited leakage into Secondary Containment form Primary Containment, the amount of iodine will be limited, since it will stay in solution. This results in less dose to the public from iodine.
Notes: <number>
<number>
<number>

## Slide 10
<number>
CONTAINMENT (CONT)
Fermi primary containment: GE Mark I design
The Drywell is normally inerted with nitrogen during power operation (prevents hydrogen/oxygen explosion).
Major components are:
  Drywell
  Torus
  8 vent pipes
  Eighty 24 inch diameter downcomer pipes
Notes: <number>
<number>
<number>

## Slide 11
CONTAINMENT (CONT)
<number>
Major components of the CONT system
Drywell - An inverted light bulb shaped steel pressure vessel with a spherical lower portion (68 ft. diameter) and a cylindrical upper portion (39 ft. in diameter). The DW is enclosed and supported by the concrete reactor building.
Torus - Steel pressure vessel in the shape of a donut, located below and encircling the drywell. Diameter is 112 feet, with a cross sectional diameter of 30 ft. Contains approx. 1,000,000 gallons of water, with net air space above the water pool of approx. 128,000 ft3.
Vent Piping - 8 vent pipes connect DW and Torus, each is 6 feet in diameter. Vent pipes connect to a header located in the air space within the torus. Projecting downward from this header are 80 downcomer pipes terminating 3 ft. below the surface of the water in the torus pool.
Notes: <number>
<number>
<number>

## Slide 12
<number>
CONTAINMENT (CONT)
Pipe break inside drywell (or LOCA) would result in:
  Reactor water and steam would be released into the drywell.
  Increased DW pressure would force a mixture of nitrogen, steam, and water through the vents into pool of water in torus.
  Steam would condense in the suppression pool, gradually heating up the suppression pool water.
    Heat is removed from SP by RHR in the Torus Cooling mode.
Notes: <number>
<number>
<number>

## Slide 13
CONTAINMENT (CONT)
<number>
Residual steam in the DW would create a vacuum as it cools, resulting in SP water being drawn up into downcomer piping.
  Vacuum breakers are installed to assure torus pressure does not exceed drywell pressure by more than 0.5 psid.
  This limits the water slug which would be ejected into the suppression pool on a subsequent steam blowdown.
Notes: <number>
<number>
<number>

## Slide 14
<number>
CONTAINMENT (CONT)
SQUIB valve
Notes: <number>
<number>
<number>

## Slide 15
CONTAINMENT (CONT)
<number>
The CONT pumps are normally lined up to CONT storage tank in Standby condition
When an emergency situation requires CONT, Operators start the system by placing the control room switch to "Start Sys A" or "Start Sys B"
  Selected pump starts
  Both explosive valves actuate
  An isolation signal is sent to RWCU System to isolate the outboard valve (F004), which trips the RWCU pumps (This is provided to prevent the removal of the CONT solution from the reactor )
  Indication of proper operation of CONT by Pump run light in Control Room, Storage tank level decreasing, Loss of continuity alarm on squib valves and Check valve F006 OPEN
Notes: <number>
<number>
<number>

## Slide 16
<number>
CONTAINMENT (CONT)
Notes: <number>
<number>
<number>

## Slide 17
CONTAINMENT (CONT)
<number>
Refuel Outage system testing – including verification of Squib valve operation and flowpath
EAV
REACTOR
Sodium Pentaborate solution
FI
PI
Test Tank
System actuated with suction lined up to test tank – verifies proper flowrate by tank level change over time
Notes: <number>
<number>
<number>

## Slide 18
CONTAINMENT (CONT)
<number>
Quarterly pump / system performance testing – suction and return to CONT Test Tank
EAV
REACTOR
Sodium Pentaborate solution
FI
PI
Test Tank
Notes: <number>
<number>
<number>

## Slide 19
<number>
Review
TERMINAL OBJECTIVE
Students will understand the CONT system , its major components and flowpaths
CONTAINMENT (CONT)
Notes: <number>
<number>
<number>

## Slide 20
<number>
Review
ENABLING OBJECTIVES
State the purpose of the CONT system, including its importance to nuclear safety.
Using a simplified diagram, identify and explain the purpose of the major components and equipment of the CONT system.
Identify the modes of operation of the CONT system, including the major components and flowpaths associated with each mode.
Describe the basic interrelationships between the CONT system and other plant systems.
Describe the manner in which the CONT system can shutdown the reactor in the event of failure of normal reactor controls
CONTAINMENT (CONT)
Notes: <number>
<number>
<number>

## Slide 21
CONTAINMENT (CONT)
<number>
QUESTIONS???
Notes: <number>
<number>
<number>