## Slide 1
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 2
Outline
A. Introduction to concept of commercial building energy auditing
  1. Why energy efficiency (EE) is important
  2. Energy use and waste in commercial building operations
  3. Prioritizing energy efficiency over renewable energy generation
B. Ordinances, policies and standards governing commercial building audits
  1. San Francisco Existing Commercial Buildings Performance Ordinance
  2. State of California energy goals
  3. ASHRAE standards, including Building Energy Assessment Professional (BEAP)
  4. Other audit standards
C. Three ASHRAE audit levels
  1. Preliminary energy use analysis
  2. Level 1, Walk-through analysis
  3. Level 2, Intermediate, energy survey and energy analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
E. Elements in preliminary analysis of building performance data
  1. Engineering and architectural document review
  2. Geographical and climatic review
  3. Review and analysis of current energy use and costs
  4. Benchmarking procedures
F. Factors in on-site building assessment
  1. Common safety hazards and field safety techniques
  2. Occupant interviews and assessment of building operations
  3. Building envelope
  4. Electrical systems
  5. HVAC&R systems
  6. Lighting systems and use
  7. Miscellaneous other energy use systems
  8. Domestic water systems and use
  9. Indoor environmental quality
G. Analysis of data collected
  1. Identify opportunities for efficiency improvement
  2. Calculate value of efficiency improvements and return on investment
  3. Prioritize options based on client criteria
H. Audit completion activities
  1. Prepare and present written report
  2. Assist with development of implementation plan
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 3
C. Three ASHRAE audit levels
  Preliminary energy use analysis
  Level 1, Walk-through analysis
  3. Level 2, Intermediate, Energy survey and analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 4
Introduction to Commercial Building Audits
Course No. ENRG 50
ashrae.org

## Slide 5
Introduction to Commercial Building Audits
Course No. ENRG 50
ashrae.org

## Slide 6
C. Three ASHRAE audit levels
  Preliminary energy use analysis
  Level 1, Walk-through analysis
  3. Level 2, Intermediate, Energy survey and analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 7
Course No. ENRG 50
Summary - Preliminary energy use analysis
1. Preliminary energy use analysis
    Analyze historic utility use and cost
    Develop the Energy Utilization Index (EUI)
    Compare the building EUI to similar buildings
    - Energy Star/ CBECs
    - Energy IQ (www.energyiq.lbl.gov)
    Determine if further engineering study and analysis are likely to produce significant energy savings
    EUI: annual energy use per square foot (kBtu/ft2/yr)
    reading material: http://cms.ashrae.biz/EUI/
    http://www.energystar.gov/index.cfm?fuseaction=buildingcontest.eui

## Slide 8
Course No. ENRG 50
Steps - Preliminary energy use analysis
1. Preliminary energy use analysis
    1. Potential customer interface and information
    - Customer goals
    - Previous energy conservation projects
    - Schedule of facilities
    - Maintenance polices
    2. Determine the gross conditioned square footage, classify the primary use

## Slide 9
Course No. ENRG 50
Steps - Preliminary energy use analysis
1. Preliminary energy use analysis
    3. Review of utility data (12-36 months)
    - Analyze data and trend
    - Compare the EUI and cost index with similar buildings
    - Determine potential of EEMs
    - Determine potential local utility rebate programs

## Slide 10
Course No. ENRG 50
Steps - Preliminary energy use analysis
1. Preliminary energy use analysis
    EUI
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf

## Slide 11
Course No. ENRG 50
EPA Portfolio Manager – Energy Star ratings
1. Preliminary energy use analysis
● Baseline
● Level 1 Improvements
● Level 2 Improvements
● Level 3 Improvements

## Slide 12
Course No. ENRG 50
Report - Preliminary Energy Use Analysis
1. Preliminary energy use analysis
Provide description of facility, occupancy, floor area, usage and scheduling etc
Present graph of utility bills, analysis and summary tables
Present results of benchmarking
Present preliminary list of potential EEMs for further analysis

## Slide 13
C. Three ASHRAE audit levels
  Preliminary energy use analysis
  Level 1, Walk-through analysis
  3. Level 2, Intermediate, Energy survey and analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 14
Course No. ENRG 50
Summary - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    Assess a building’s energy cost and efficiency by analyzing energy bills and conducting a brief on-site survey
    Identify and provide a savings and analysis of low-cost/no-cost measures.
    Provide a list of potential capital improvements that merit further consideration

## Slide 15
Course No. ENRG 50
Steps - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    1. Complete steps of a Preliminary energy use analysis
    2. Potential customer interface and information
    - compare drawing to actual facility conditions
    - ask customer goals/concerns
    - equipment replacement history and plans
    - operation and scheduling
    - maintenance procedures

## Slide 16
Course No. ENRG 50
Steps - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    3. Perform a brief walk-through survey of the facility
    - occupancy information
    - envelope components (wall, roof, windows, doors, skylights, floor, etc)
    - HVAC systems inventory and control strategies
    - lighting fixtures and controls
    - other energy usage systems
    4. Perform a rough estimate to determine the approximate breakdown of energy use for significant end-use categories

## Slide 17
Course No. ENRG 50
Steps - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    5. Identify savings and cost analysis for low-cost/no-cost measures
    - lighting retrofits having fastest payback
    - better control systems or strategies
    - obvious energy wasting operation and poor scheduling
    - utility and local government rebates in cost analysis

## Slide 18
Course No. ENRG 50
Steps - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    6. Provide a list of potential capital improvement EEMs for further analysis
    - building envelope features (tinting or installing insulated windows, roof insulation)
    - HVAC retrofits including higher efficiency equipment, VFD for fans/pumps
    - lighting retrofit requiring significant investment such as LED, system controls
    - building automation controls

## Slide 19
Course No. ENRG 50
Report - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    contents in preliminary energy use analysis
    preliminary end use energy breakdown estimation
    discussion of irregularities found in the energy use patterns
    summary of special problems or needs identified for operational or maintenance procedures
    list of low-cost/no-cost EEMs and estimate of savings
    list of potential capital improvement EEMs with initial estimate of energy savings and costs.

## Slide 20
Course No. ENRG 50
Report - Level 1: Walk-through analysis
2. Level 1, Walk-through analysis
    Sample report
    http://campusops.uoregon.edu/files/pdf/admin/knight-law-ashrae-level-1-june-11.pdf

## Slide 21
C. Three ASHRAE audit levels
  Preliminary energy use analysis
  Level 1, Walk-through analysis
  3. Level 2, Intermediate, Energy survey and analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 22
Course No. ENRG 50
Summary - Level 2: Intermediate
3. Level 2, Intermediate, energy survey and analysis
    includes a more detailed building survey and energy analysis
    provide a breakdown of the energy use
    Identify and provide the savings and cost analysis of all practical measures, along with a discussion of any changes to operation and maintenance procedures
    Provide a list of potential capital-intensive improvements that require more thorough data collection and engineering analysis, and a judgment of potential costs and savings
    This level of analysis will be adequate for most buildings and measures

## Slide 23
Course No. ENRG 50
Steps - Level 2: Intermediate
    1. Complete steps of a Level 1 walk-through analysis services
    2. Potential customer interface and information
    - corporate financial criteria and guidelines
    - discuss potential energy conservation projects to compliment equipment replacement plans, anticipated changes to operation and schedule of equipment and facilities
    - status of current equipment, validation of operational controls, existing problems areas, actual maintenance level of implementation
3. Level 2, Intermediate, energy survey and analysis

## Slide 24
Course No. ENRG 50
Steps - Level 2: Intermediate
    3. Existing building survey information
    - occupancy information, equipment schedules and operations
    - envelope components (wall, roof, windows, doors, skylights, floor, etc)
    - HVAC systems inventory and control strategies
    - lighting fixture types, quantities and controls
    - other energy usage systems
3. Level 2, Intermediate, energy survey and analysis

## Slide 25
Course No. ENRG 50
Steps - Level 2: Intermediate
    4. Breakdown of energy use within building
    - provide estimate based on California Commercial End-use Survey
    - conduct preliminary energy analysis with energy simulation software (eQuest, Trane Tracer or Carrier HAP-Wizard level, etc)
    Selection of energy analysis software
    http://www1.eere.energy.gov/buildings/qualified_software.html
3. Level 2, Intermediate, energy survey and analysis

## Slide 26
eQuest demo

## Slide 27
eQuest demo

## Slide 28
eQuest demo

## Slide 29
eQuest demo

## Slide 30
Take eQuest intro- and intermediate training classes at the Pacific Energy Center, they are FREE!

## Slide 31
Course No. ENRG 50
Steps - Level 2: Intermediate
    5. Identify recommended changes to equipment, operation and maintenance activities, cost/savings estimates.
    6. Provide energy savings and cost analysis of practical EEMs that meet customer’s constraints and capital improvement criteria
    - building envelope features (windows, skylights, etc)
    - HVAC retrofits – replacement of existing systems by higher efficiency equipment, VFD, building automation controls
    - Lighting retrofits – re-lamping, de-lamping
    Include utility rebates in cost analysis
3. Level 2, Intermediate, energy survey and analysis

## Slide 32
Course No. ENRG 50
Steps - Level 2: Intermediate
    7. Provide a list of capital-intensive improvements that require further data and analysis
    - building envelope features (better wall, cool roof etc)
    - HVAC retrofits – complete replacement of existing systems, significant upgrade to building automation controls
    - Lighting retrofits requiring significant investment such as LED light sources for high bay and light poles
    - renewable energy generation systems like solar PV, solar thermal, etc
    Include utility rebates in cost analysis
3. Level 2, Intermediate, energy survey and analysis

## Slide 33
Course No. ENRG 50
Report - Level 2: Intermediate
    1. Provide summary of energy use and cost associated with major components
    2. Specify computer software analysis utilized, compare actual total utility usage and calculated energy estimates
    3. Provide description of building including floor plans, and inventories of major equipment
3. Level 2, Intermediate, energy survey and analysis

## Slide 34
Course No. ENRG 50
Report - Level 2: Intermediate
    4. Provide discussion of recommended energy conservation measures.
    - existing situations that are wasting energy
    - required repairs of existing equipment
    - impact of measures on health, safety and comfort
    - impact on occupants, O&M procedures and staff
    - useful life of equipment
    - an outline of any new skills required for existing employees or new hires as a result of EEM implementation
3. Level 2, Intermediate, energy survey and analysis

## Slide 35
Course No. ENRG 50
Report - Level 2: Intermediate
    5. Provide summary (tables) with:
    - name of EEMs
    - estimated annual energy savings
    - estimated installation cost, simple payback period
    - implementation plan for all recommendation EEMs
    6. Recommend EEMs and verification methods to validate performance of projects
    7. Discuss potential capital-intensive measures requiring a level 3 analysis
3. Level 2, Intermediate, energy survey and analysis

## Slide 36
Course No. ENRG 50
Report - Level 2: Intermediate
    Sample Level 2 report:
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf
3. Level 2, Intermediate, energy survey and analysis

## Slide 37
Course No. ENRG 50
Report Demo – Executive Summary
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf
3. Level 2, Intermediate, energy survey and analysis

## Slide 38
Course No. ENRG 50
Report Demo – Executive Summary
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf
3. Level 2, Intermediate, energy survey and analysis

## Slide 39
Course No. ENRG 50
Report Demo – Executive Summary
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf
3. Level 2, Intermediate, energy survey and analysis

## Slide 40
C. Three ASHRAE audit levels
  Preliminary energy use analysis
  Level 1, Walk-through analysis
  3. Level 2, Intermediate, Energy survey and analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 41
Course No. ENRG 50
Summary - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    Focuses on capital-intensive projects identified during Level 2 analysis
    Involves more detailed field data gathering as well as a more rigorous engineering analysis
    Provides detailed project cost and savings calculations with a high level of confidence sufficient for major capital investment decisions

## Slide 42
Course No. ENRG 50
Steps - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    1. Complete steps of a Level 2 energy survey and analysis
    2. Potential customer interface and information
    - customer provide detail financial criteria for life cycle cost analysis and 3rd party financing as applicable
    - discuss potential construction contractor and maintenance contractors that can assist with cost estimated for detailed analysis

## Slide 43
Course No. ENRG 50
Steps - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    3. Existing building on-site survey information, validate drawings and other documentation
    - envelope components (wall, roof, windows, doors, skylights, floor, etc)
    - HVAC systems components and control strategies
    - lighting fixtures and controls
    - equipment schedules, space and occupancy information
    - other energy usage systems

## Slide 44
Course No. ENRG 50
Steps - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    4. Conduct more rigorous energy analysis
    - conduct energy simulation analysis (i.e. Trane Tracer or Carrier HAP-Detail level)
    - requires well defined building envelope information
    - detail HVAC systems components and control strategies
    - accurate lighting and other electrical equipment levels and schedules

## Slide 45
Course No. ENRG 50
Steps - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    5. Detail construction costs estimates or contractor price quotes are obtained
    6. Equipment O&M and replacement costs are determined from service contractors
    7. Complete life cycle cost analysis of alternatives are conducted
    - Life Cycle Costing Manual – Federal
    - Energy Management Program

## Slide 46
Course No. ENRG 50
Report - Level 3: Detailed analysis
4. Level 3, Detailed analysis of capital-intensive modifications
    1. Include text, schematics and equipment list necessary to completely describe the EEMs.
    2. Preliminary engineering information and detailed estimates or firm price quotes should support cost estimates.
    3. Prepare a financial evaluation of the estimated capital improvement projected energy savings
    4. Use the owner’s chosen techniques and criteria as requested in final presentation

## Slide 47
Course No. ENRG 50
Difference between levels
4. Level 3, Detailed analysis of capital-intensive modifications
Process | 1 | 2 | 3
Conduct Preliminary Energy Analysis (PEA) |  |  | 
Conduct walk-through survey |  |  | 
Identify low-cost/no-cost recommendations |  |  | 
Identify capital improvements |  |  | 
Review M&E design, condition and O&M practices |  |  | 
Measure key parameters |  |  | 
Analyze capital measures (savings & costs including interaction) |  |  | 
Meet with owner/operators to review recommendations |  |  | 
Conduct additional testing/monitoring |  |  | 
Perform detailed system modeling |  |  | 
Provided schematic layouts for recommendations |  |  | 
Source from kW Engineering

## Slide 48
Course No. ENRG 50
Difference between levels
4. Level 3, Detailed analysis of capital-intensive modifications
Report | 1 | 2 | 3
Estimate savings from utility rate change |  |  | 
Compare EUI to that of similar sites |  |  | 
Summarize utility data |  |  | 
Estimate savings if EUI met target |  |  | 
Estimate low-cost/no-cost savings |  |  | 
Perform detailed end-use breakdown |  |  | 
Estimate capital project costs and savings |  |  | 
Complete building description and equipment inventory |  |  | 
General description of considered measures |  |  | 
Recommended M&V method |  |  | 
Financial analysis of recommended EEMs |  |  | 
Detailed description of recommended measures |  |  | 
Detailed EEM cost estimates |  |  | 
Source from kW Engineering

## Slide 49
Course No. ENRG 50
Homework:
    Read through sample auditing reports