## Slide 1
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 2
Outline
A. Introduction to concept of commercial building energy auditing
  1. Why energy efficiency (EE) is important
  2. Energy use and waste in commercial building operations
  3. Prioritizing energy efficiency over renewable energy generation
B. Ordinances, policies and standards governing commercial building audits
  1. San Francisco Existing Commercial Buildings Performance Ordinance
  2. State of California energy goals
  3. ASHRAE standards, including Building Energy Assessment Professional (BEAP)
  4. Other audit standards
C. Three ASHRAE audit levels
  1. Preliminary energy use analysis
  2. Level 1, Walk-through analysis
  3. Level 2, Intermediate, energy survey and energy analysis
  4. Level 3, Detailed analysis of capital-intensive modifications
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
E. Elements in preliminary analysis of building performance data
  1. Engineering and architectural document review
  2. Geographical and climatic review
  3. Review and analysis of current energy use and costs
  4. Benchmarking procedures
F. Factors in on-site building assessment
  1. Common safety hazards and field safety techniques
  2. Occupant interviews and assessment of building operations
  3. Building envelope
  4. Electrical systems
  5. HVAC&R systems
  6. Lighting systems and use
  7. Miscellaneous other energy use systems
  8. Domestic water systems and use
  9. Indoor environmental quality
G. Analysis of data collected
  1. Identify opportunities for efficiency improvement
  2. Calculate value of efficiency improvements and return on investment
  3. Prioritize options based on client criteria
H. Audit completion activities
  1. Prepare and present written report
  2. Assist with development of implementation plan
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 3
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 4
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 5
Course No. ENRG 50
Objectives of the audit, including needed data & resources
1. Objectives of the audit, including needed data and resources
    http://www.nrel.gov/docs/fy06osti/38601.pdf

## Slide 6
Course No. ENRG 50
Before starting the audit, define the audit criteria
1. Objectives of the audit, including needed data and resources
    Audit objectives
    Audit type
    Audit methodology and standards
    Staff involvement
    Site or utility boundary
    Timeline
    Reporting requirements

## Slide 7
Course No. ENRG 50
Audit objectives
1. Objectives of the audit, including needed data and resources
    Objectives
    - understand how energy is used within the facility
    - find opportunities for improvement and energy saving
    - evaluate the effectiveness of an energy efficiency project or program

## Slide 8
Course No. ENRG 50
Available resources
1. Objectives of the audit, including needed data and resources
    Staff and experience
    Time
    Tools and software
    The budget for conducting the energy audit
    Government or utility incentive programs

## Slide 9
Course No. ENRG 50
Make an audit plan
1. Objectives of the audit, including needed data and resources
    Scope of the audit
    - customer’s expectations
    - building function
    - typical EEMs for similar facilities and businesses
    Time of the audit and its duration, milestone for each step
    Elements of the audit that have a high priority
    Responsibilities and tasks of each audit team member
    Format of the audit report and its outline

## Slide 10
Course No. ENRG 50
Preparing an audit checklist
1. Objectives of the audit, including needed data and resources
    Steps to be taken during the energy audit
    Data and information that should be collected
    Existing measurement instrument and the data recorded
    Required measurements during the energy audit and the list of parameters to be measured
    Major equipment to be assessed in more detail
    List of main components of the results section of the audit report, for guidance
    Other major concerns and considerations

## Slide 11
Course No. ENRG 50
Collecting energy bills and available data/information
1. Objectives of the audit, including needed data and resources
    12-36 months of utility bills
    Building function and usage allocation
    Climatic data for the period in which the auditing is conducted
    Possible archived records with measurements from existing recorders
    Architectural and engineering plans of the plant and its equipment
    Status of energy management and any energy-saving measures implemented
    General information about the plant (year of construction, ownership status, renovations, types of products, operation schedule, operating hours, scheduled shut-downs, etc.)

## Slide 12
Course No. ENRG 50
Collecting energy bills and available data/information
1. Objectives of the audit, including needed data and resources
    Building function and usage allocation
    http://www.uos.harvard.edu/fmo/building_maintenance/quincy_house_energy_audit.pdf

## Slide 13
Course No. ENRG 50
Energy bill analysis
1. Objectives of the audit, including needed data and resources
    CA utility distribution
http://www.energy.ca.gov/maps/serviceareas/CA_Electric_IOU.pdf
http://www.energy.ca.gov/maps/serviceareas/natural_gas_detailed_service_areas.pdf

## Slide 14
Course No. ENRG 50
Electric rates & charges (PG&E)
1. Objectives of the audit, including needed data and resources
    Fixed and variable costs
    Rate schedule
    Season
    Demand charge
    TOU
    Energy charge
    PF charge
    Credits
    More Utility info: http://www.energy.ca.gov/maps/
Calculate energy use per day
- electricity: kWh/day
- natural gas: therms/day
Check the utility’s updated tariff sheet!
PG&E: http://www.pge.com/tariffs/
A separate course about utility rates

## Slide 15
Course No. ENRG 50
PG&E – Electric rate schedules (partial)
1. Objectives of the audit, including needed data and resources
PG&E: http://www.pge.com/tariffs/

## Slide 16
Course No. ENRG 50
PG&E rate schedule demo - A10
1. Objectives of the audit, including needed data and resources
http://www.pge.com/tariffs/tm2/pdf/ELEC_SCHEDS_A-10.pdf

## Slide 17
Course No. ENRG 50
PG&E rate schedule demo - A10
1. Objectives of the audit, including needed data and resources
http://www.pge.com/tariffs/tm2/pdf/ELEC_SCHEDS_A-10.pdf
Reading link: Understanding your bill
http://www.pge.com/includes/docs/pdfs/b2b/newgenerator/understandingyourbill_residential.pdf

## Slide 18
Course No. ENRG 50
PG&E rate schedule demo - A10
1. Objectives of the audit, including needed data and resources
http://www.pge.com/tariffs/tm2/pdf/ELEC_SCHEDS_A-10.pdf

## Slide 19
Course No. ENRG 50
PG&E – Gas rate schedules (partial)
1. Objectives of the audit, including needed data and resources
http://www.pge.com/tariffs/GRS.SHTML#GRS

## Slide 20
Course No. ENRG 50
PG&E rate schedule demo – G-NR1
1. Objectives of the audit, including needed data and resources
http://www.pge.com/tariffs/tm2/pdf/GAS_SCHEDS_G-NR1.pdf

## Slide 21
Course No. ENRG 50
California building climate zones
1. Objectives of the audit, including needed data and resources
http://www.energy.ca.gov/maps/renewable/building_climate_zones.html
CZ 1: Arcata CZ 2: Santa Rosa CZ 3: Oakland CZ 4: Sunnyvale CZ 5: Santa Maria CZ 6: Los Angeles CZ 7: San Diego CZ 8: El Toro CZ 9: Pasadena CZ10: Riverside CZ11: Red Bluff CZ12: Sacramento CZ13: Fresno CZ14: China Lake CZ15: El Centro CZ16: Mount Shasta
http://www.energy.ca.gov/maps/renewable/Climate_Zones_by_City.pdf

## Slide 22
Course No. ENRG 50
Homework
1. Objectives of the audit, including needed data and resources
    Assuming you are going to audit the college building, generate a questionnaire to collect needed data & information.

## Slide 23
Course No. ENRG 50
Initial walk-through visit
1. Objectives of the audit, including needed data and resources
    Meet with executive, energy and/or facility manager(s)
    Interview facility staff if necessary and possible
    Become familiar with the facility
    Establish a common understanding of the audit process
    Observe the existing control strategies
    Determine the processes that will need a detailed audit later

## Slide 24
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 25
Course No. ENRG 50
Assessment management
2. Assessment management
    preliminary walk-through, analysis
    instrument inventory and functions
    collect / monitor usage data
    analyzing energy use patterns
    Benchmarking and comparative analysis
    Identifying energy efficiency potentials
    Cost benefit analysis

## Slide 26
Course No. ENRG 50
Instrument inventory and functions
2. Assessment management
    Demo: Motor inventory
    - Site ID
    - Motor application
    - Motor location
    - Maker
    - Model#
    - Size (HP)
    - Name plate speed (RPM)
    - Measured speed (RPM)
    - % full-load
    - efficiency
    - Motor kW
    - % on
    - Operation hours/yr
    - Analyst

## Slide 27
Course No. ENRG 50
Collect/monitor usage data
2. Assessment management
    The data collection is carefully matched to the goals of the analysis and the study questions to avoid the common pitfalls of too little or too much data.
A. Select performance metrics to be measured.
B. Identify data required for each metric.
C. Specify physical location of each measurement.
D. Specify frequency of each measurement.
E. Specify measurement equipment.
F. Determine practicality of measurements.
G. Estimate cost of DAS equipment and operation.
H. Calculate uncertainty of measurements.
I. Resolve cost and uncertainty with expectations

## Slide 28
Course No. ENRG 50
Select performance metrics to be measured
2. Assessment management
    NREL Tier 2 measurement planning forms: http://www.nrel.gov/docs/fy06osti/38601.pdf
# | Performance Metric | Neces-sary Data | Measurement/ Source of data | Record Freq. | Measurement equipment | 
 |  |  |  |  | Devices | Quantity
1 | Gross interior floor area |  |  | 1 time | N/A | N/A
2 | Functional Area |  |  | 1 time | N/A | N/A
3 | Installed lighting energy use |  |  | series |  | 
4 | Plug-in lighting energy use |  |  |  |  | 
5 | Façade lighting energy use |  |  | series |  | 
6 | Building lighting energy use |  |  | series |  | 
7 | Heating energy use |  |  | series |  | 
8 | Cooling energy use |  |  | series |  | 
9 | Air distribution energy use |  |  | Series |  | 
10 | Cold storage transfer |  |  | series |  | 

## Slide 29
Course No. ENRG 50
Select performance metrics to be measured – ctnd.
2. Assessment management
    NREL Tier 2 measurement planning forms: http://www.nrel.gov/docs/fy06osti/38601.pdf
# | Performance Metric | Neces-sary Data | Measurement/ Source of data | Record Freq. | Measurement equipment | 
 |  |  |  |  | Devices | Quantity
11 | Other HVAC energy use |  |  | series |  | 
12 | HVAC energy use |  |  | series |  | 
13 | DHW energy use |  |  | series |  | 
14 | DHW load |  |  | series |  | 
15 | DHW system efficiency |  |  | monthly |  | 
16 | Plug loads energy use |  |  | series |  | 
17 | People-Mover energy use |  |  | series |  | 
18 | Other building energy use |  |  | series |  | 
19 | Building energy use |  |  | Series |  | 
20 | Building energy use intensity |  | N/A | annual | N/A | N/A

## Slide 30
Course No. ENRG 50
Select performance metrics to be measured – ctnd.
2. Assessment management
    NREL Tier 2 measurement planning forms: http://www.nrel.gov/docs/fy06osti/38601.pdf
# | Performance Metric | Neces-sary Data | Measurement/ Source of data | Record Freq. | Measurement equipment | 
 |  |  |  |  | Devices | Quantity
21 | Building purchased energy cost |  | bills | monthly | N/A | N/A
22 | Building purchased energy cost intensity |  | N/A | annually | N/A | N/A
23 | Building electrical demand |  | N/A | monthly | N/A | N/A
24 | Building electrical demand intensity |  | N/A | monthly | N/A | N/A
25 | Process energy use |  |  | Series |  | 
26 | Outdoor energy use |  |  | series |  | 
27 | Cogeneration fuel use |  |  | series |  | 
28 | Cogeneration electrical energy output |  |  | series |  | 
29 | Cogeneration thermal energy output |  |  | Series |  | 
30 | Cogeneration losses |  | N/A | Series | N/A | N/A

## Slide 31
Course No. ENRG 50
Select performance metrics to be measured – ctnd.
2. Assessment management
    NREL Tier 2 measurement planning forms: http://www.nrel.gov/docs/fy06osti/38601.pdf
# | Performance Metric | Neces-sary Data | Measurement/ Source of data | Record Freq. | Measurement equipment | 
 |  |  |  |  | Devices | Quantity
31 | PV energy production |  |  | series |  | 
32 | Wind energy production |  |  | series |  | 
33 | Other electrical energy production |  |  | series |  | 
34 | Electrical generation system losses |  |  | series |  | 
35 | Thermal energy production |  |  | Series |  | 
36 | Produced energy storage transfer |  |  | series |  | 
37 | Facility energy production |  |  | series |  | 
38 | Total facility energy use |  |  | series |  | 
39 | Net facility energy use |  |  | Series |  | 
40 | Net facility purchased energy cost |  | bills | Monthly | N/A | N/A

## Slide 32
Course No. ENRG 50
Select performance metrics to be measured – ctnd.
2. Assessment management
    NREL Tier 2 measurement planning forms: http://www.nrel.gov/docs/fy06osti/38601.pdf
# | Performance Metric | Neces-sary Data | Measurement/ Source of data | Record Freq. | Measurement equipment | 
 |  |  |  |  | Devices | Quantity
41 | Total facility electrical demand |  |  | monthly | N/A | N/A
42 | Net facility electrical demand |  |  | monthly | N/A | N/A
43 | Net facility load factor |  |  | monthly | N/A | N/A
44 | Indoor zone temperature |  |  | Series |  | 
45 | Outdoor ambient temperature |  |  | Series |  | 
 | User-defined metrics |  |  |  |  | 

## Slide 33
Course No. ENRG 50
10 Common problems in Energy Audits
2. Assessment management
    http://home.comcast.net/~tureston2011/BES/Audit_Tool/10_CommonProblemsInEnergyAudits.pdf

## Slide 34
D. Developing the scope of work in a commercial building audit
  1. Objectives of the audit, including needed data and resources
  2. Assessment management
  3. Responsibilities of audit team members
Introduction to Commercial Building Audits
Course No. ENRG 50

## Slide 35
Course No. ENRG 50
Responsibilities of audit team members
3. Responsibilities of audit team members
    Project manager
    - communicate with customers
    - plan and keep the project on track
    - organize installation of data-loggers and data collection
    - integrate EEMs and report together
    - write executive summary and summarize financial section

## Slide 36
Course No. ENRG 50
Responsibilities of audit team members
3. Responsibilities of audit team members
    Lighting analysis
    HVAC systems and controls
    - This area is highly technical; well-trained personnel are essential
    Building envelope
    - Civil engineering and architecture background are preferred.
    Simulation analysis
    Other specialties: such as kitchen EE experts for restaurants
One may conduct more than one task.
Each one needs to finish analysis and writing for his/her own sections.