## Slide 1
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 2
Outline
A. Introduction to fundamentals of lighting
  Lighting terminology
  Physics and principles of lighting
  Units of measurement
  Vision and colors
  Ambient, directional and task lighting
  Over- and under-illuminance
B. Lighting systems
  Components
  Types of lamps
  Ballasts
  Lamp comparison matrix
  Types of lighting luminaires and intensities
  Energy efficiency measures (EEMs)
C. Lighting controls
  Basic concepts of effectiveness of lighting control
  Types and appropriate applications of lighting controls
  Lighting control equations
  Energy efficiency measures (EEMs)
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
E. Lighting measurements
  Tools
  Data loggers and applications
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Method of calculating skylight energy savings
G. Lighting standards, codes and regulations
  Underwriters' Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
H. O&M measures to assure optimal performance
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 3
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 4
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 5
Course No. ENRG 54
De-lamping
    The removal of one or more lamps from a luminaire
    Save energy (kWh), reduce demand (kW), save maintenance parts and labor.
    May combine with re-lamping
    Strategies:
    - reduce # of fixtures
    - de-lamp 4- or 3-lamp fixtures
    - retrofit
1. De-lamping

## Slide 6
Course No. ENRG 54
De-lamp 4- or 3-lamp fixtures
    Quite often offices, schools, warehouses are overlighted
    Pay attention to the lighting level after de-lamping
    Pay attention to # of ballast and wiring
    May combined with reflector installation
1. De-lamping

## Slide 7
Course No. ENRG 54
Case study
    A warehouse has 50 fixtures of 48”, four (4) T8 lamps with 2 electronic ballast in series. The lighting level is 60 fcd. Delamping in half will still provide acceptable light, according to IES illumination level standard, assuming the lighting pattern is distributed well through out the area.
    The fixtures have 4 units of 32W T8 and 2 units of 10W electric ballasts. Working time is 4700 hours a year. It takes 15 minutes to delamp a fixture, and the labor cost is $35/hour. If the average Energy rate is $0.15/kWh, and Demand rate is $10/kW, calculate:
    Total energy savings
    Simple payback period
    Other saving
1. De-lamping

## Slide 8
Course No. ENRG 54
Case study
    1. Total energy savings
    Energy savings = ((2X32W)+(1X10W))/1000 X 50 X 6000h X $0.15 /kWh =$ 3330/yr
    Demand saving = ((2X32W)+(1X10W))/1000X50 X$10X 12 months = $444/yr
    Total energy savings = $3330 + $444 = $3774/yr
    2. Simple payback period
    Implementation cost = $35/hr X 50 fixtures X (15 min/ 60 min per hr) = $ 437.5
    Simple payback period = $437.5/$3774 = 0.12 yr = 1.4 months
    3. Other savings
    Lamp replacement parts and labor
1. De-lamping

## Slide 9
Course No. ENRG 54
Retrofit – fluorescent troffer
1. De-lamping

## Slide 10
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 11
Course No. ENRG 54
Scotopic lighting
http://www.neweralighting.com/What%20is%20scotopic%20lighting.html
250 W HPS vs. 100 W Inductions 175 W HPS vs. 80 W Induction
Refers to the “whiter” or “cooler” color temperature
Human eye’s ability to see more clearly and further across a whiter light
Reduces visual fatigue when viewing a computer screen
2. Scotopic lighting

## Slide 12
Course No. ENRG 54
Scotopic lighting
2. Scotopic lighting

## Slide 13
Course No. ENRG 54
Ratio of scotopic to photopic (S/P ratio)
2. Scotopic lighting

## Slide 14
Course No. ENRG 54
Scotopic lighting
    Reading materials:
    http://www.lightenergysource.com/Scotopic.htm
    http://www.solarlight.com/products/Energyconservationscotopic.pdf.pdf
2. Scotopic lighting

## Slide 15
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 16
Course No. ENRG 54
Task and ambient light level
    Decoupling ambient lighting and task lighting
    In office, provide uniform low-level ambient lighting with individually controlled task fixtures
    Task lighting gives the user maximum control
    Reading material:
    http://www.dazor.com/benefits.html
Michaelsenergy.com
3. Task and ambient light level

## Slide 17
Course No. ENRG 54
Task and ambient light level
    Example: a work environment can maintain lower levels of overhead light by illuminating desktops with energy-efficient task lights. Considering an office with 16 workstations illuminated by 16 overhead fixtures each with four T8 32-watt fluorescents.
    The total wattage = 16 X 4 X 32 W = 2,048W.
    If each fixture used two T8 instead of four, and each workstation was equipped with an 18-watt task light,
    The new wattage = 16 X 2 X 32 + 18 X 16 = 1312 W
    Energy consumption would be reduced by 36 percent!
3. Task and ambient light level

## Slide 18
Course No. ENRG 54
Task and ambient light level
http://www.emsd.gov.hk/emsd/e_download/pee/Task_Lighting_Design.pdf
3. Task and ambient light level

## Slide 19
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 20
Course No. ENRG 54
Circadian rhythms
Biological process that displays an endogenous, entrainable oscillation of ~24hrs.
©wikipedia.com

## Slide 21
Course No. ENRG 54
Circadian rhythms – general criteria:
    Around the day - the rhythms repeat in a 24-hr period
    Endogenous - the rhythms persist in the absence of external cues
    Entrainable - the rhythms can be adjusted to match the local time
    Temperature compensation – the rhythms maintain circadian periodicity over a range of physiological temperatures
4. Circadian rhythms

## Slide 22
Course No. ENRG 54
Circadian rhythms
    Allow organisms to anticipate and prepare for precise and regular environmental changes
    Can be disrupted by the wrong timing, intensity and/or spectral composition of light
    Lighting needs to be designed in a way that is “circadian rhythm friendly”
    An example: dimming and Kelvin changing LED troffers
4. Circadian rhythms

## Slide 23
Course No. ENRG 54
    Homework 2 discussion
Chapter C homework project:
Design lighting control strategies for a campus space: e.g. conference room, hall way, restroom, classroom, office. Requirement:
choose the right type(s) of controls, explain why.
choose the proper physical place to install, explain why.