## Slide 1
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 2
Outline
A. Introduction to fundamentals of lighting
  Lighting terminology
  Physics and principles of lighting
  Units of measurement
  Vision and colors
  Ambient, directional and task lighting
  Over- and under-illuminance
B. Lighting systems
  Components
  Types of lamps
  Ballasts
  Lamp comparison matrix
  Types of lighting luminaires and intensities
  Energy efficiency measures (EEMs)
C. Lighting controls
  Basic concepts of effectiveness of lighting control
  Types and appropriate applications of lighting controls
  Lighting control equations
  Energy efficiency measures (EEMs)
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
E. Lighting measurements
  Tools
  Data loggers and applications
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Method of calculating skylight energy savings
G. Lighting standards, codes and regulations
  Underwriters' Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
H. O&M measures to assure optimal performance
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 3
G. Lighting standards, codes and regulations
  Underwriters’ Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 4
G. Lighting standards, codes and regulations
  Underwriters’ Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 5
Course No. ENRG 54
Underwriters’ Laboratory (UL)
UL is an independent, non-profit product safety testing and certification organization.
Testing includes:
- Risk of fire
- Electric shock
- Injury to persons
1. Underwriters’ Laboratory (UL)

## Slide 6
Course No. ENRG 54
Underwriters’ Laboratory (UL)
UL lighting:
http://www.ul.com/global/eng/pages/offerings/industries/lighting/
Product services
- Lamps and Light Engines
- Luminaires
- Signs and Advertising
- Electronics
- LED Packages and LED Arrays
- Retrofit Kits
- Bases, Holders and Connectors
- Lenses and Optics
1. Underwriters’ Laboratory (UL)

## Slide 7
G. Lighting standards, codes and regulations
  Underwriters’ Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 8
Course No. ENRG 54
Uniform Building Codes (UBC)
A national code used mostly in the western states to regulate building standards.
Was first published in 1927 by the International Council of Building Officials, updated every 3 yrs until 1997.
Intended to promote public safety and provided standardized requirements for safe construction
Was replaced in 2000 by the new International Building code (IBC) published by the International Code Council (ICC).
2. Uniform Building Codes (UBC)

## Slide 9
Course No. ENRG 54
International Building Codes (IBC)
A model building code developed by International Code Council (ICC).
Has been adopted throughout most of the US.
Specifies the minimum acceptable level of safety for buildings.
California adopted IBC with amendments into California Building Code (CBC)
Reference link: http://www.ccidc.org/code_faq.html
2. Uniform Building Codes (UBC)

## Slide 10
Course No. ENRG 54
California Building Code (CBC)
Mandates:
- Exit lighting requirements
- Emergency egress lighting
Usually responsibility of electrical engineers
2. Uniform Building Codes (UBC)

## Slide 11
G. Lighting standards, codes and regulations
  Underwriters’ Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 12
Course No. ENRG 54
  Americans with Disabilities Act (ADA)
Gives civil rights protections to individuals with disabilities that are like those provided to individuals on the basis of race, sex, national origin, and religion.
Objects projecting from walls with their leading edges between 27” and 80” (685 mm and 2030 mm) above the finished floor (AFF) shall protrude no more than 4” (100mm) into walks, halls, corridors, passageways, or aisles
ADA web link: http://www.ada.gov/
3. Americans with Disabilities Act (ADA)

## Slide 13
G. Lighting standards, codes and regulations
  Underwriters’ Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 14
Course No. ENRG 54
  Title 24
Mandatory requirements
Prescriptive requirements
Exterior lighting regulations
California Energy commission: http://www.energy.ca.gov/
Title 24 2008: http://www.energy.ca.gov/title24/2008standards/index.html
4. Title 24 applications

## Slide 15
Course No. ENRG 54
  Title 24 – Outline of Lighting Requirements
Standard | Mandatory Measures | Prescriptive Requirement
Nonresidential | Shutoff controls Space control Exit signs Occupant sensors Daylighting controls Special controls | Lighting power (whole building and space-by-space allowances) Control credits
Residential | Luminaire efficacy controls | None
4. Title 24 applications

## Slide 16
Course No. ENRG 54
  Title 24 – Allowed Lighting Power Densities (LPD)
4. Title 24 applications

## Slide 17
Course No. ENRG 54
  Title 24 – Allowed Lighting Power Densities (LPD)

## Slide 18
Course No. ENRG 54
  Title 24 – Lighting Power Adjustment Factors
4. Title 24 applications

## Slide 19
Course No. ENRG 54
  Title 24 – Lighting Power Adjustment Factors
4. Title 24 applications

## Slide 20
Course No. ENRG 54
  Title 24 2013
California’s building efficiency standards are updated on a 3 year cycle.
Title 24 2013 takes effect in January 2014.
Compliance with new Code results in 25% less energy for lighting, heating, cooling, ventilation, and water heating than 2008 Standards.
Web link: http://www.energy.ca.gov/title24/2013standards/supporting_docs.html
4. Title 24 applications

## Slide 21
Course No. ENRG 54
  Title 24 2013 Key Requirements
Reductions in Area Category LPDs
 | 2008 T24 | 2013 T24
Open office (>250sf> | 0.9 W/sf | 0.75 W/sf
Private office (<250sf) | 1.1 W/sf | 1.0 W/sf
Retail | 1.6 W/sf | 1.2 W/sf with adders: - 0.3 W/sf for accent, display and feature lighting (must be adjustable or directional luminaires) - 0.2 W/sf for decorative lighting
4. Title 24 applications

## Slide 22
Course No. ENRG 54
  Title 24 2013 Key Requirements
New power adjustment factors for occupancy sensor control in open offices:
- 0.2 for 250-500 sf per sensor (4 people)
- 0.3 for 125-250 sf per sensor (2 people)
- 0.4 for <125 sf per sensor (1 person)
4. Title 24 applications

## Slide 23
Course No. ENRG 54
  Title 24 – Multi-level control requirements
4. Title 24 applications

## Slide 24
Course No. ENRG 54
  Title 24 2013 Key Requirements
Allowance for 24/7 lighting for building security has been removed (130.1(a) and 130.1(c)).
allowance for egress lighting have mostly been removed
- 0.2 W/sf is excepted from the Area Control requirements, along designated egress routes (130.1(a)). (previous code was 0.3W/sf)
- 0.05 W/sf is excepted from the Shut-Off Control requirements, along designated egress routes in offices only. Other building types have no allowance. (130.1(c)).(previous code was 0.3 W/sf)
4. Title 24 applications

## Slide 25
Course No. ENRG 54
4. Title 24 applications

## Slide 26
Course No. ENRG 54
  Lighting design
4. Title 24 applications

## Slide 27
Course No. ENRG 54
  Lighting design
4. Title 24 applications

## Slide 28
Outline
A. Introduction to fundamentals of lighting
  Lighting terminology
  Physics and principles of lighting
  Units of measurement
  Vision and colors
  Ambient, directional and task lighting
  Over- and under-illuminance
B. Lighting systems
  Components
  Types of lamps
  Ballasts
  Lamp comparison matrix
  Types of lighting luminaires and intensities
  Energy efficiency measures (EEMs)
C. Lighting controls
  Basic concepts of effectiveness of lighting control
  Types and appropriate applications of lighting controls
  Lighting control equations
  Energy efficiency measures (EEMs)
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
E. Lighting measurements
  Tools
  Data loggers and applications
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Equation and method of calculating skylight energy savings
G. Lighting standards, codes and regulations
  Underwriters' Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
H. O&M measures to assure optimal performance
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 29
H. Operations & Maintenance (O&M) measures to assure optimal performance
  Make sure occupancy sensors turn lights off after a reasonable period of time
  Check timer(s) and lighting schedule set-up regularly
  Override manual controls
  Daylighting commissioning
  Educate the end users in proper use of lighting controls
  Seasonally adjust exterior lighting schedule
  Re-lamp entire building on a regular schedule
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 30
Course No. ENRG 54
Daylighting commissioning
Select proper equipment
Install the sensors at proper place(s)
Calibrate sensors so they produce the desired control signal
The light sensor and controller must be adjusted to provide the desired light level at the task location.
May require professional designer(s) and/or contractor(s)