## Slide 1
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 2
Outline
A. Introduction to fundamentals of lighting
  Lighting terminology
  Physics and principles of lighting
  Units of measurement
  Vision and colors
  Ambient, directional and task lighting
  Over- and under-illuminance
B. Lighting systems
  Components
  Types of lamps
  Ballasts
  Lamp comparison matrix
  Types of lighting luminaires and intensities
  Energy efficiency measures (EEMs)
C. Lighting controls
  Basic concepts of effectiveness of lighting control
  Types and appropriate applications of lighting controls
  Lighting control equations
  Energy efficiency measures (EEMs)
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
E. Lighting measurements
  Tools
  Data loggers and applications
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Method of calculating skylight energy savings
G. Lighting standards, codes and regulations
  Underwriters' Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
H. O&M measures to assure optimal performance
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 3
E. Lighting measurements
  1. Tools
  2. Data loggers and applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 4
  1. Tools
  - Flicker checker
  - Illuminance meter
  - Luminance meter
  - Spectrophotometer
  - Goniophotometer
  - Circuit tracer
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 5
Course No. ENRG 54
Flicker checker – check types of ballast
    Spin to check the type of ballast
    Magnetic -- see patterns spinning in opposing directions
    Electronic – continuous circles
    Why: secondary frequency
    Multiple light sources could affect the result
    Alternative tool: discriminator
    - green: electronic
    - red: magnetic
1. Tools

## Slide 6
Course No. ENRG 54
Illuminance meter
    For “incident” light level readings (fcd or lux)
    1 fcd = 10 lux
    Normally need to average several spots
Konicaminolta.com
1. Tools

## Slide 7
Course No. ENRG 54
Luminance meter
    For reading reflected or transmitted “brightness” (in cd/m2)
    Specifies the brightness of a luminous surface and/or a light source
    reading materials: http://www.konicaminolta.com/instruments/products/light/luminance-meter/ls100-ls110/index.html
Konicaminolta.com
1. Tools

## Slide 8
Course No. ENRG 54
Spectrophotometer
    Measures light intensity as a function of the light source wavelength
    Measures spectral reflectance of objects
    Reading materials: http://senze-instruments.com/gl-optic-mini-spectrometer--.html
Mini-spectrometer
1. Tools

## Slide 9
Course No. ENRG 54
Goniphotometer
    Measure the light emitted from luminaires and lamps at different angles
    reading materials: http://wiki.answers.com/Q/What_is_the_principle_of_goniophotometer ;
    http://www.pro-lite.uk.com/File/goniophotometers.php
Wikipedia.com
1. Tools

## Slide 10
Course No. ENRG 54
Circuit tracer
    Used to find wiring indoors and outdoors
    Consists of a probe, transmitter and receiver
    Performs tests w/o having to interrupt power
http://www.licensedelectrician.com/Store/Circuit_Tracers.htm
1. Tools

## Slide 11
D. Lighting measurements
  1. Tools
  2. Data loggers and applications
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 12
  2. Data loggers and applications
  Occupancy
    -Used to determine energy saving potential by recording when a space is occupied/vacant, and when lighting is on/off
  Hours of use
  Multiple channels
  pay attention where to install
Course No. ENRG 54
Introduction to Lighting Systems and Controls
http://www.onsetcomp.com
2. Data loggers and applications

## Slide 13
Course No. ENRG 54
Occupancy
2. Data loggers and applications

## Slide 14
Course No. ENRG 54
Occupancy
2. Data loggers and applications

## Slide 15
Course No. ENRG 54
Laboratory project 1
    Learn how to use selected tools covered in this chapter
2. Data loggers and applications

## Slide 16
Course No. ENRG 54
Homework 3
    Design data logger experiment – determine what you want to test
    Decide the right type of logger and proper place to install
    Install data logger
    Load data logger data onto computer
    Plot figure by Excel
    Find potential problem
    Come up a solution
    Write a report
2. Data loggers and applications