## Slide 1
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 2
Outline
A. Introduction to fundamentals of lighting
  Lighting terminology
  Physics and principles of lighting
  Units of measurement
  Vision and colors
  Ambient, directional and task lighting
  Over- and under-illuminance
B. Lighting systems
  Components
  Types of lamps
  Ballasts
  Lamp comparison matrix
  Types of lighting luminaires and intensities
  Energy efficiency measures (EEMs)
C. Lighting controls
  Basic concepts of effectiveness of lighting control
  Types and appropriate applications of lighting controls
  Lighting control equations
  Energy efficiency measures (EEMs)
D. Additional EEMs
  De-lamping
  Scotopic lighting
  Task and ambient light levels
  Circadian rhythms
E. Lighting measurements
  Tools
  Data loggers and applications
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Method of calculating skylight energy savings
G. Lighting standards, codes and regulations
  Underwriters' Laboratory (UL)
  Uniform Building Code (UBC)
  Americans with Disabilities Act (ADA)
  Title 24 applications
H. O&M measures to assure optimal performance
Introduction to Lighting Systems and Controls
Course No. ENRG 54

## Slide 3
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Equation and method of calculating skylight energy savings
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 4
Course No. ENRG 54
Zonal Cavity Procedure (Lumen Method)
1. Zonal Cavity Formula
E ave = Average Illuminance (fc)
CU = Luminaire Coefficient of Utilization
LLF = Light loss factor
Zonal Cavity Formula

## Slide 5
Course No. ENRG 54
Luminaire Coefficient of Utilization
Depends on Room Cavity Ratio (RCR) and room reflectance
Accounts for the percentage of light that will reach the workplane from a given luminaire under specific room conditions
Requires user to make assumptions about ceiling and wall reflectances
Requires user to calculate RCR
1. Zonal Cavity Formula

## Slide 6
Course No. ENRG 54
Room Cavity Ratio (RCR)
h = Distance from luminaire plane to work plane
L = Room length
W = Room width
P = Room perimeter
or
1. Zonal Cavity Formula

## Slide 7
Course No. ENRG 54
Light Loss Factors (LLF)
Recoverable LLFs
- Lamp Lumen Depreciation (LLD)
- Luminaire Dirt Depreciation (LDD)
- Room Surface Dirt Depreciation (RSDD)
Non-Recoverable LLF
- Ballast factor
- Voltage
Total LLF = LLD X LDD X RSDD X BF X Other LLFs
1. Zonal Cavity Formula

## Slide 8
Course No. ENRG 54
Zonal Cavity Procedure (Lumen Method)
Provides a single value of average illuminance
Advantages
- Provides a quick, easy way to estimate illuminance or fixture quantities needed
- An easy means of comparing different luminaires or lamps
1. Zonal Cavity Formula

## Slide 9
Course No. ENRG 54
Another Use for Lumen Method
To determine the number of luminaires rquired to achieve an average illuminance:
Eave = Average Illuminance (fc)
CU = Luminaire Coefficient of Utilizaiton
LLF = Light loss factor
1. Zonal Cavity Formula

## Slide 10
Course No. ENRG 54
Point by Point Calculations
Useful for determining illuminance at a specific point
Accounts for angle of incidence
Requires knowledge of inverse square law and basic trig. Functions
Limitations
- Labor intensive
- Requires separate calculation for each point
- Applicable for point sources
- Does not account for interreflections
1. Zonal Cavity Formula

## Slide 11
Course No. ENRG 54
Inverse Square Law
Basic equation to find illuminace
Where
E = targe Illuminance (fc)
I = Source Intensity (cd)
D = Distance from Source to Target (ft)
D
I
E
1. Zonal Cavity Formula

## Slide 12
Course No. ENRG 54
Inverse Square Law
Horizontal illuminace – source at an angle:
Where
Eh = targe Illuminance (fc)
I = Source Intensity (cd)
D = Distance from Source to Target (ft)
θ = Angle of incidence
D
θ
E
h
1. Zonal Cavity Formula

## Slide 13
Course No. ENRG 54
Inverse Square Law
Vertical illuminace – source at an angle:
Where
E = targe Illuminance (fc)
I = Source Intensity (cd)
D = Distance from Source to Target (ft)
θ = Angle of incidence
D
θ
E
v
1. Zonal Cavity Formula

## Slide 14
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Equation and method of calculating skylight energy savings
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 15
Course No. ENRG 54
Energy saving equation
    Power = The Rate of Consumption kilowatts kW
Time = The Duration of Consumption
Energy = Power X Time
= Total Consumption in Kilowatt hours kWh
Control strategy: regulate the rate of consumption (power), or the duration of consumption (time), or both.
2. Equation and method of calculating energy savings

## Slide 16
Course No. ENRG 54
Energy saving calculation
2. Equation and method of calculating energy savings
Energy = Power X Time = Total kWh
If reducing power only (e.g. de-lamping, re-lamping):
∆ Energy = ∆ Power X Time = (Power1– Power2 )X Time2
If reducing time only (e.g. installing occupancy sensor):
∆ Energy = Power X ∆Time = Power X (Time1 – Time2)
If both power and time reduced (e.g. daylighting control)
∆ Energy = Power1 X Time1 – Power2 X Time2

## Slide 17
Course No. ENRG 54
Excel practice
2. Equation and method of calculating energy savings
∆ Energy = ∆ Power X Time = (Power1– Power2 )X Time2
∆ Energy = Power X ∆Time = Power X (Time1 – Time2)
∆ Energy = Power1 X Time1 – Power2 X Time2
Simple payback period = estimated cost / annual savings

## Slide 18
Course No. ENRG 54
Excel hands-on practice
2. Equation and method of calculating energy savings
Combining with data logger results, students will calculate energy savings by Excel (at the end of this section)

## Slide 19
F. Lighting calculations
  Equation and method of calculating lumens (zonal cavity formula)
  Equation and method of calculating energy savings
  Method of calculating skylight energy savings
Course No. ENRG 54
Introduction to Lighting Systems and Controls

## Slide 20
Course No. ENRG 54
Skylights
3. Method of calculating skylight energy savings
Provide excellent lighting conditions to the interior of buildings
Reduce the use of electric lighting, to save energy and reduce peak electric loads when combined with photocontrols
Satisfy human needs for contact with outdoors
Increase safety and security with highly reliable daytime lighting
Provide emergency smoke vents
Americanhistory.si.edu

## Slide 21
Course No. ENRG 54
Considerations when designing skylights
3. Method of calculating skylight energy savings
Visual and thermal comfort
Seasonal and daily shifts in daylight availability
Heat loss and heat gain
Integration with the electric lighting system
Choice of daylighting control strategy
Integration with the roofing system
Integration with the HVAC design
Utility costs and peak electric demand
Structural and safety concerns

## Slide 22
Course No. ENRG 54
How skylights save energy?
3. Method of calculating skylight energy savings
Cons :
- Provide adequate daylight to turn off electric lights
- Add less heat to a space and reduce cooling
Pros:
- Allow more heat to escape through the roof
- Increase cooling loads by letting more sun’s heat in.
The optimum balance is a function of the building design, the building operation, and the local climatic conditions.

## Slide 23
Course No. ENRG 54
Who need skylights?
3. Method of calculating skylight energy savings
Buildings with large open areas.
- retail stores and shopping malls
- grocery stores
- schools
- single-story office buildings
- manufacturing
- warehouses
- distribution centers
- agricultural building

## Slide 24
Course No. ENRG 54
% of commercial buildings in California?
3. Method of calculating skylight energy savings
Retail buildings 18%
Grocery Stores 8.5%
Schools 8.5%
Small offices 5.0%
Warehouses 12%
---------------------------------------
Total 52%
Significant energy saving opportunities by skylights.

## Slide 25
Course No. ENRG 54
Related materials – Skylighting Guidelines
3. Method of calculating skylight energy savings
http://www.energydesignresources.com/resources/publications/design-guidelines/design-guidelines-skylighting-guidelines.aspx
http://apps1.eere.energy.gov/buildings/publications/pdfs/commercial_initiative/toplighting_final_report.pdf

## Slide 26
Course No. ENRG 54
SkyCalc – Skylight design tool
Readily available data for most of California Climate Zones
Built-in basic lighting calculations, energy cost analysis, and other useful information
Makes skylight sizing quick and easy
Accounts for:
- Heating
- Cooling
- Lighting
- Energy rates
- Occupancy/use
3. Method of calculating skylight energy savings
http://www.energydesignresources.com/resources/software-tools/skycalc.aspx

## Slide 27
Course No. ENRG 54
SkyCalc: example input characteristics
3. Method of calculating skylight energy savings

## Slide 28
Course No. ENRG 54
SkyCalc: example input characteristics
3. Method of calculating skylight energy savings