## Slide 1
HVAC Fundamentals & Components
Course No. ENRG 55A

## Slide 2: HVAC Fundamentals & Components Outline
A – Introduction to physical principles of HVAC & systems
  Conversion of units
  Concept of work, power, and energy
  Overview of psychrometric analysis of the air conditioning
  Thermodynamic laws and heat transfer principles
  Estimate of sensible and latent heat changes
  Analysis of thermal comfort
B – Load calculations
  Heating loads
  Cooling load
  Use of psychrometric tables and various software packages for heating and cooling estimates
C – Conveyance systems
  Principles of conveyance systems
  Types of conveyance equipment and components
  Nameplate data interpretation
D – Principles of heating systems
  Types of heating equipment & components
  Nameplate data interpretation
E – Cooling systems
  Principles of the refrigeration cycle
  Types of equipment & components
  Nameplate data interpretation
F – Air-handling systems
  Diffusers, and registers
  Dampers, louvers, filters, fans

## Slide 3: HVAC Fundamental & Components
Introduction to physical principles of HVAC & systems
  Conversion of units
    Temperature
    Pressure
    Horse power
    Power (kWh)
    British Thermal Units/hr (BTU/hr)
    Tons
  Concept of work, power, and energy
  Overview of psychrometric analysis of the air conditioning system
    Psychrometric processes and calculations
      Sensible or latent processes
      Air side equation
      Air side mixing
      Summary of process line calculations
    Room sensible heat ratio (RSHR) & room cubic feet per minutes (CFM)
      Room sensible heat ratio
      Room sensible heat ratio line
      Design CFM (CFM)
      Multiple room sensible heat ratios
    The coil sensible heat ratio (CSHR)
      Coil sensible heat ratio without ventilation
      Coil sensible heat ratio ventilation
      Construction of the RSHR & CSHR
      Coil By-pass factor
      Thermodynamic laws and heat transfer principles
      Estimate of sensible and latent heat changes
      Analysis of thermal comfort

## Slide 4: HVAC Fundamental & Components
Conversion of Units
Temperature:
Definition: It is a thermodynamic property that indicates heat intensity or the amount of heat level in a substance or process. Heat intensity could be coldness or hotness.
Temperature scale: A thermometer is the instrument used to measure the temperature of a substance
Types of Thermometers: Celsius, Fahrenheit, Kelvin, and Rankine
System of International (SI) Units
Celsius scale: Measures ice point of water at 0oC and boiling point of water at 100oC
Kelvin scale: Measures ice point of water at 273oK and boiling point of water at 373oK. However, Kelvin scale measure absolute zero (0oK) is (-273oC) on the Celsius scale
English System Units (US Customary Units)
Fahrenheit scale: Measures ice point of water at 32oF and boiling point of water at 212oF
Rankine scale: Measures ice point of water at 492oR and boiling point of water at 672oR;
In addition, Rankine scale absolute zero temperature at 0oR is -460oF on Fahrenheit scale
NB: Absolute zero temperature is the temperature set point when all molecules cease to move.

## Slide 5: HVAC Fundamental & Components
Temperature conversions

## Slide 6: HVAC Fundamentals & Components
Temperature: Fahrenheit to Celsius conversion
Equations for temperature conversions
(1)
(2)
or
(3)
Example (1):
Convert 20oC to Fahrenheit degrees (oF)
Solution
Using equation 2 or 3

## Slide 7: HVAC Fundamental & Components
Equations for Celsius to Kelvin conversion and Fahrenheit to Rankine
(4)
(5)
Example (2): Example (3)
Convert 82oF to Rankine degrees Convert 104oF to Kelvin degrees
Solution: Solution:
From equation (5) From equation (1) Also using Equation (4)
(1)

## Slide 8: HVAC Fundamental & Components
Exercises on temperature conversions
Problem 1:
Convert the following Celsius temperature readings to equivalent temperatures on the Fahrenheit scale:
-76oC
95oC
-115oC
Problem 2:
In a manufacturing process, the temperature passing across a heating coil is increased from 40oF to 160oF. Estimate the temperature rise in degrees Celsius.
Problem 3:
Convert the following temperatures in Kelvin to equivalent temperatures in degrees Rankine
125oK
210oK

## Slide 9: HVAC Fundamentals & Components
b. Pressure unit conversion
Definition: Pressure is defined as a measure of the intensity of a force at any given point on the contact surface or in short, we say pressure is force exerted on a substance per unit area. Units for pressure include: inches mercury, inHg; inches water column, inwc or inches water gauge, inwg; pound per square inches, lbf/in2, or lbf/ft2, Pascal, etc.
Mathematically, we’ve
There are three types of pressures used to describe fluid (air, water etc.) in motion. These include: Static Pressure (SP), Velocity Pressure (VP) and Total Pressure (TP)
Mathematically, we’ve
Where: TP = the total pressure which is the sum of static and velocity pressures
SP = the static pressure is the pressure of the fluid at rest. It is calculated by using “Bernoulli’s Equation” or measured by manometers, barometers, Bourdon tube gages etc.
Where: SP =
This flow energy equation applied to flow in a duct and pipe

## Slide 10: HVAC Fundamental & Components
VP = the velocity pressure is used to measure velocities and flow rates in piping and ducts.
VP can be calculated using the equation , from Bernoulli’s Equation
VP is measured using pitot tube
Notes: http://www.engineeringtoolbox.com/pitot-tubes-d_612.html

## Slide 11: HVAC Fundamental & Components

## Slide 12: HVAC Fundamental & Components
Notes: http://boomeria.org/physicslectures/pascal/pascal.html

## Slide 13: HVAC Fundamental & Components
b. Pressure conversion cont’d
1. Convert 16.2 ft air to inches water gage (in wg)
Solution:
Using conversion factor: 1 in.wg = 69.6 ft.air
2. Change the following quantities to the new units specified
130 lbf/in2 (psi) to ft wg
25 in. Hg to mm. Hg
Exercise:
Convert 20.5 in. Hg to lbf/in2(psi)
Apply the following units conversion factors:
US Customary: Metric System/SI Systems:
2.036 in. Hg = 1 lbf/in2 (psi) 1 Pa = 1 N/m2
1 psi = 2.3 ft. wg 101.3 kN/m2 = 1 atm
3386 Pa = in Hg
249.1 Pa = 1 mm Hg
Metric/SI systems – US Customary:
1 atm – 14.7 psia
1 atm – 760 mm Hg

## Slide 14: HVAC Fundamental & Components
b. Pressure conversion cont’d
Given: 130 lbf/in2 to ft wg B. Convert 25 inHg to 1 mmHg

## Slide 15: HVAC Fundamental & Components
b. Pressure conversion continued
There are five types of pressure; namely: Pressure gage, vacuum pressure; atmospheric pressure and absolute pressure
    Pressure gage (Pgage): measures pressure in closed systems such as pipes, ducts, vessels etc.
    Vacuum pressure: (Pvac): It is the pressure that is measured below the atmospheric pressure
    Atmospheric pressure: Patm: It is the pressure occupied by the weight of the atmosphere (universe). At the “Sea Level”, the pressure is measured at approximately 14.696 psia (101,325 Pascal) and the value decreases as the “Altitude” atmosphere increases.
    Absolute pressure (Pabs) : It total of gage pressure and atmospheric pressure
    Zero Pressure also known as perfect vacuum is an area of space that has no pressure.
Mathematical Relationship Between: Pabs, Patm, Pgage and Pvac

## Slide 16: HVAC Fundamental & Components
Illustration
Measured pressure
Measured pressure
Atmospheric pressure
Zero Pressure
Patm
Pabs
Pabs
Pvac

## Slide 17: HVAC Fundamental & Components
b. Pressure conversion continued
Example
The gages on suction gas and discharge gas lines of a pump is 10 psiv (lb/in2 vac) and 65 psig, respectively. What is the pressure increase by the pump?
Solution: Illustration
Mathematically
Exercise
The pressure gage connected to the discharge of a cooling tower pump in Pharmaceutical Company in Emeryville, Oakland, California reads 28psig. Calculate the absolute water pressure at the pump discharge?
A 250 ft vertical pipe in a high-rise building is filled with chilled water. Estimate the pressure in psig that a valve in the bottom of the line will have to withstand.
10psiv
65psig
75psig
Atmospheric pressure
Suction pressure gage
reading
Discharge pressure
gage reading
Zero pressure
10psiv
65psig
Pump
Suction
Discharge

## Slide 18: HVAC Fundamental & Components
c. Horse power conversion
Definition: One horsepower is the work done at a rate of 550 poundforce-foot per second or 33000 poundforce –foot per minute, which is equivalent to 745.7 watts
Mathematically
Example:
Convert 11840 lbf--ft/min to horsepower (hp)
Solution:
Exercise: Convert 250 hp to lbf-ft/s .