## Slide 1
HVAC Fundamentals & Components
Course No. ENRG 55A

## Slide 2: HVAC Fundamentals & Components Outline
A – Introduction to physical principles of HVAC & systems
  Conversion of units
  Concept of work, power, and energy
  Overview of psychrometric analysis of the air conditioning
  Thermodynamic laws and heat transfer principles
  Estimate of sensible and latent heat changes
  Analysis of thermal comfort
B – Load calculations
  Heating loads
  Cooling load
  Use of psychrometric tables and various software packages for heating and cooling estimates
C – Conveyance systems
  Principles of conveyance systems
  Types of conveyance equipment and components
  Nameplate data interpretation
D – Principles of heating systems
  Types of heating equipment & components
  Nameplate data interpretation
E – Cooling systems
  Principles of the refrigeration cycle
  Types of equipment & components
  Nameplate data interpretation
F – Air-handling systems
  Diffusers, and registers
  Dampers, louvers, filters, fans

## Slide 3: HVAC Fundamentals & Components
Introduction to physical principles of HVAC & systems
  Conversion of units
    Temperature
    Pressure
    Horse power
    Power (kWh)
    British Thermal Units/hr (BTU/hr)
    Tons
  Concept of work, power, and energy
  Overview of psychrometric analysis of the air conditioning system
    Psychrometric processes and calculations
      Sensible or latent processes
      Air side equation
      Air side mixing
      Summary of process line calculations
    Room sensible heat ratio (RSHR) & room cubic feet per minutes (CFM)
      Room sensible heat ratio
      Room sensible heat ratio line
      Design CFM (CFM)
      Multiple room sensible heat ratios
    The coil sensible heat ratio (CSHR)
      Coil sensible heat ratio without ventilation
      Coil sensible heat ratio ventilation
      Construction of the RSHR & CSHR
      Coil By-pass factor
      Thermodynamic laws and heat transfer principles
      Estimate of sensible and latent heat changes
      Analysis of thermal comfort

## Slide 4: HVAC Fundamentals & Components
Conversion of Units
Temperature:
Definition: It is a thermodynamic property that indicates heat intensity or the amount of heat level in a substance or process. Heat intensity could be coldness or hotness.
Temperature scale: A thermometer is the instrument used to measure the temperature of a substance
Types of Thermometers: Celsius, Fahrenheit, Kelvin, and Rankine
System of International (SI) Units
Celsius scale: Measures ice point of water at 0oC and boiling point of water at 100oC
Kelvin scale: Measures ice point of water at 273oK and boiling point of water at 373oK. However, Kelvin scale measure absolute zero (0oK) is (-273oC) on the Celsius scale
English System Units (US Customary Units)
Fahrenheit scale: Measures ice point of water at 32oF and boiling point of water at 212oF
Rankine scale: Measures ice point of water at 492oR and boiling point of water at 672oR;
In addition, Rankine scale absolute zero temperature at 0oR is -460oF on Fahrenheit scale
NB: Absolute zero temperature is the temperature set point when all molecules cease to move.

## Slide 5: HVAC Fundamentals & Components
Temperature conversions

## Slide 6: HVAC Fundamentals & Components
Temperature: Fahrenheit to Celsius conversion
Equations for temperature conversions
(1)
(2)
or
(3)
Example (1):
Convert 20oC to Fahrenheit degrees (oF)
Solution
Using equation 2 or 3

## Slide 7: HVAC Fundamentals & Components
Equations for Celsius to Kelvin conversion and Fahrenheit to Rankine
(4)
(5)
Example (2): Example (3)
Convert 82oF to Rankine degrees Convert 104oF to Kelvin degrees
Solution: Solution:
From equation (5) From equation (1) Also using Equation (4)
(1)

## Slide 8: HVAC Fundamentals & Components
Exercises on temperature conversions
Problem 1:
Convert the following Celsius temperature readings to equivalent temperatures on the Fahrenheit scale:
-76oC
95oC
-115oC
Problem 2:
In a manufacturing process, the temperature passing across a heating coil is increased from 40oF to 160oF. Estimate the temperature rise in degrees Celsius.
Problem 3:
Convert the following temperatures in Kelvin to equivalent temperatures in degrees Rankine
125oK
210oK

## Slide 9: HVAC Fundamentals & Components
b. Pressure unit conversion
Definition: Pressure is defined as a measure of the intensity of a force at any given point on the contact surface or in short, we say pressure is force exerted on a substance per unit area. Units for pressure include: inches mercury, inHg; inches water column, inwc or inches water gauge, inwg; pound per square inches, lbf/in2, or lbf/ft2, Pascal, etc.
Mathematically, we’ve
There are three types of pressures used to describe fluid (air, water etc.) in motion. These include: Static Pressure (SP), Velocity Pressure (VP) and Total Pressure (TP)
Mathematically, we’ve
Where: TP = the total pressure which is the sum of static and velocity pressures
SP = the static pressure is the pressure of the fluid at rest. It is calculated by using “Bernoulli’s Equation” or measured by manometers, barometers, Bourdon tube gages etc.
Where: SP =
This flow energy equation applied to flow in a duct and pipe

## Slide 10: HVAC Fundamentals & Components
VP = the velocity pressure is used to measure velocities and flow rates in piping and ducts.
VP can be calculated using the equation , from Bernoulli’s Equation
VP is measured using pitot tube
Notes: http://www.engineeringtoolbox.com/pitot-tubes-d_612.html

## Slide 11: HVAC Fundamentals & Components

## Slide 12: HVAC Fundamentals & Components
Notes: http://boomeria.org/physicslectures/pascal/pascal.html

## Slide 13: HVAC Fundamentals & Components
b. Pressure conversion cont’d
1. Convert 16.2 ft air to inches water gage (in wg)
Solution:
Using conversion factor: 1 in.wg = 69.6 ft.air
2. Change the following quantities to the new units specified
130 lbf/in2 (psi) to ft wg
25 in. Hg to mm. Hg
Exercise:
Convert 20.5 in. Hg to lbf/in2(psi)
Apply the following units conversion factors:
US Customary: Metric System/SI Systems:
2.036 in. Hg = 1 lbf/in2 (psi) 1 Pa = 1 N/m2
1 psi = 2.3 ft. wg 101.3 kN/m2 = 1 atm
3386 Pa = in Hg
249.1 Pa = 1 mm Hg
Metric/SI systems – US Customary:
1 atm – 14.7 psia
1 atm – 760 mm Hg

## Slide 14: HVAC Fundamentals & Components
b. Pressure conversion cont’d
Given: 130 lbf/in2 to ft wg B. Convert 25 inHg to 1 mmHg

## Slide 15: HVAC Fundamentals & Components
b. Pressure conversion continued
There are five types of pressure; namely: Pressure gage, vacuum pressure; atmospheric pressure and absolute pressure
    Pressure gage (Pgage): measures pressure in closed systems such as pipes, ducts, vessels etc.
    Vacuum pressure: (Pvac): It is the pressure that is measured below the atmospheric pressure
    Atmospheric pressure: Patm: It is the pressure occupied by the weight of the atmosphere (universe). At the “Sea Level”, the pressure is measured at approximately 14.696 psia (101,325 Pascal) and the value decreases as the “Altitude” atmosphere increases.
    Absolute pressure (Pabs) : It total of gage pressure and atmospheric pressure
    Zero Pressure also known as perfect vacuum is an area of space that has no pressure.
Mathematical Relationship Between: Pabs, Patm, Pgage and Pvac

## Slide 16: HVAC Fundamentals & Components
Illustration
Measured pressure
Measured pressure
Atmospheric pressure
Zero Pressure
Patm
Pabs
Pabs
Pvac

## Slide 17: HVAC Fundamentals & Components
b. Pressure conversion continued
Example
The gages on suction gas and discharge gas lines of a pump is 10 psiv (lb/in2 vac) and 65 psig, respectively. What is the pressure increase by the pump?
Solution: Illustration
Mathematically
Exercise
The pressure gage connected to the discharge of a cooling tower pump in Pharmaceutical Company in Emeryville, Oakland, California reads 28psig. Calculate the absolute water pressure at the pump discharge?
A 250 ft vertical pipe in a high-rise building is filled with chilled water. Estimate the pressure in psig that a valve in the bottom of the line will have to withstand.
10psiv
65psig
75psig
Atmospheric pressure
Suction pressure gage
reading
Discharge pressure
gage reading
Zero pressure
10psiv
65psig
Pump
Suction
Discharge

## Slide 18: HVAC Fundamentals & Components
c. Horse power conversion
Definition: One horsepower is the work done at a rate of 550 poundforce-foot per second or 33000 poundforce –foot per minute, which is equivalent to 745.7 watts
Mathematically
Example:
Convert 11840 lbf--ft/min to horsepower (hp)
Solution:
Exercise: Covert 250 hp to lbf-ft/s .

## Slide 19: HVAC Fundamentals & Components
c. Horse power conversion cont’d
1. There are two types of horsepower (hp). These include:
(a) Water Horsepower (WHP)
(b) Brake Horsepower (BHP)
2. Mathematical Formulae for WHP and BHP
a. Water horsepower is the power transmitted to a fluid or it is the power output
or or
Where:
WHP = Water horsepower, hp
Q = Flow rate, Gallons per minute (GPM) or cubic feet per sec (ft3/s )
H = Total pump head, ft
s.gfluid = Specific gravity of the fluid, for water s.g = 1
fluid = Specific weight, lbf/ft3; for water specific weight = 62.4lbf/ft3

## Slide 20: HVAC Fundamentals & Components
c. Horse power conversion cont’d
b. Brake horsepower is the power required to drive the pump or it is also known as power input.
Mathematically:
Example:
A chilled water pump used for air conditioning system in the Financial District , San Francisco, CA is delivering 250 GPM at a total head 40 ft of water. The manufacturer’s specifications for the pump efficiency is 60% at this operating condition. What is the minimum size motor that should be used to drive the pump?
Solution:
The 4.2 hp would be the minimum power needed for the motor, but in a real world a larger size motor might be used to prevent possible overloading of the motor (You may choose 5hp).

## Slide 21: HVAC Fundamentals & Components
d. Power (W) conversion:
The units for power Metric or SI systems is the watts that is equivalent to
To convert
Example: Convert 30 hp to kW.
Solution:
Exercise: Work done by motor is 260 lbf-ft/s on a particular day. What is kW for this motor.

## Slide 22: HVAC Fundamentals & Components
e. British Thermal Units (BTU) conversion
A BTU is a unit of measurement of thermal or heat energy. The capacity of an electrical equipment is usually expressed in watts (W) or kilowatts (kW) rather than BTU/hr
Conversion factors:
Power Units
3.410 BTU/hr = 1000 W
3410 BTU/hr = 1kW
2545 BTU/hr = 1hp
Energy Units
1 BTU = 778 lbf-ft
1 BTU = 1055 J = 252 calories (cal)
Example: Convert the following quantities to the new units specifies
3000W to BTU/hr
20, 000 BTU/hr to kW

## Slide 23: HVAC Fundamentals & Components
e. British Thermal Units (BTU) conversion
Solution:
Exercise:
Estimate the size electric heater kW must be used to supply 250 BTU/hr.
How many BTU/hr will a 20 kW electric heater supply?

## Slide 24: HVAC Fundamentals & Components
f. Tons conversion
It is a unit of weight of an object, which is approximately equal to 2000 lbf
Conversion factors:
1 ton = 2000 lbf = 12000 Btu/hr
Example: Convert 10 tons of refrigeration unit into BTU/hr
Solution:
Exercise: Change 1000 Btu/hr to poundforce

## Slide 25: HVAC Fundamentals & Components
2. Concept of Work, Power & Force
Work
Work is done mechanically when a force acting on an object moves the object through a distance.
Mathematically:
Example: A chilled water pump having a weight of 220 lbf is hoisted 185 ft from the ground to the top floor of a building. Calculate work done ignoring friction and other losses.

## Slide 26: Power
Power
Mechanical power is defined as rate of doing work.
Mechanical power is measured in horsepower (hp); The conversion factors and equations for mechanical power is either
Estimate the power required to pump 300 gallons per minute (gpm) of water up to a storage tank located a vertical distance of distance of230 ft above the ground. Assume water density to be 8.33 lbf/gal

## Slide 27: Energy
Energy:
Definition: Energy is the ability or capacity to work. The amount of energy required to do a given amount of work is always exactly equal to the amount of work done.
On the other hand, the amount of energy in a body is always equal to the amount of work the body can do in passing the energy from one position or condition to another.
Unit of Energy = lbf-ft
Types of Energy:
There are two types of energies: (1) Kinetic Energy; (2) Potential Energy
Kinetic Energy is the energy a body possesses by virtue of its motion or velocity
Mathematically:

## Slide 28: Energy Cont’d
Potential Energy: It is the energy a body possesses due to its position or configuration.
Potential Energy = Mass x Height
Potential Energy, lbf-ft
Mass, lbf
Height, ft
Total External Energy: It is the sum of its Kinetic Energy (KE) and Potential Energy (PE)
Total Energy = KE + PE
Example: Calculate the total external energy of 1lbf of water flowing at a rate of 60 ft/s in a manufacturing company located 200 ft above a reference datum
Solution:

## Slide 29: Psychrometric Processes Overview

## Slide 30: Outline of Psychrometric Chart

## Slide 31: Overview of Psychometric Analysis of the Air Conditioning Systems
a. Psychrometric processes and calculations
1. Sensible or Latent Processes
Notes: http://www.engineeringtoolbox.com/heating-humid-air-d_693.html
http://www.cibsejournal.com/cpd/2009-10/
http://what-when-how.com/energy-engineering/psychrometrics-energy-engineering/
http://www.practicalpsychrometric.com/sensible-heating.html
http://hpac.com/departments/design-solutions/roll-presses-indirect-cooling-0212/
http://www.jacco.com/media/AAONAire65.html
http://www.new-learn.info/packages/clear/thermal/buildings/active_systems/ac/process.html
http://www.taftan.com/thermodynamics/AIRCOND.HTM
http://www.buildingcontrolworkbench.com/Portals/1/GrayBook/Gpsychum.htm

## Slide 32: Sensible or Latent Process Cont’d
Notes: http://www.practicalpsychrometric.com/cooling-equipment-selection-05.html
http://www.arca53.dsl.pipex.com/index_files/psy20.htm

## Slide 33: Combined Sensible and Latent Processes

## Slide 34: Air Side Equations
Once any process line is drawn on the psychrometric chart, the sensible, latent, and total loads associated with that process can be calculated by using the following air equations:

## Slide 35: Air Side Equations Cont’d

## Slide 36: Summary of Process Line Calculations
Notes: http://www.docstoc.com/docs/4877065/SENSIBLE-HEAT-RATIO-Qs-Qt-PSYCHROMETRIC-CHART-Normal-Temperature

## Slide 37: Summary of Process Line Calculations Cont’d

## Slide 38: Summary of Process Line Calculations Cont’d

## Slide 39: Air Mixing Process
Equations of Mixing Air Streams

## Slide 40: Air Mixing Sample Question
Example: Outside Air (OA) and Return Air (RA) as shown are mixed. Find the mixed air (MA) Dry Bulb (DB) and Wet Bulb (WB).
Using the equations

## Slide 41: Room Sensible Heat Ratio (RSHR)

## Slide 42: Room Sensible Heat Ratio (RSHR)
Example: The following rooms are maintained at 75oF DB, and 55% RH. Estimate the RSHR of each room and average RSHR of all the rooms.
Btu/hr Room 1 Room 2 Room 3
Sensible Heat 8,000 10,500 15,000
Latent Heat 1,000 2,000 4,000
Solution:

## Slide 45: Room Sensible Heat Ratio (RSHR)
1. Room Sensible Heat Ratio (RSHR)
It is defined as the ratio of room (or zone) sensible heat to room (or zone) total heat.
Graphically & Mathematically

## Slide 46: Room Sensible Heat Ratio (RSHR)
2. Room Sensible Heat Ratio Line:
The RSHR line is define as the line drawn through the room conditions with the room sensible heat ratio slope RSCL/RTCL.
Example: Macdonald Restaurant has a sensible cooling load of 45,000 BTU/hr and a latent cooling load of 15,000 BTU/hr. The restaurant is maintained at 77oF DB and 45% RH. Draw the RSHR line.
Solution:

## Slide 47: Room Sensible Heat Ratio (RSHR)
3. Design cubic feet per minutes (CFM) Room:
The amount of supply air (CFM) is required to offset the room sensible and latent loads is determined by sensible heat equation below:
4. Selecting Supply Air Temperature
To select the optimum supply air temperature, the designer must consider the following:
Packaged DX equipment can be expected to produce air temperatures leaving the coil which are 15oF to 20oF below the room temperature.
Chilled water coils can produce air temperatures leaving the coil which are 15oF to 25oF below the room temperature.
Larger difference between the room temperature and supply CFM and save fan power
Lower coil temperatures will reduce the coefficient of performance (COP) of the refrigeration equipment.

## Slide 48: Room Sensible Heat Ratio (RSHR)
4. Selecting Supply Air Temperature
5. The lowest theoretical supply temperature is equal to the apparatus dew point which is located at the intersection of the RSHR line and the saturation line.
6. In actual practice, a supply air condition which falls on the RSHR line and has a relative humidity between 85% and 95% is a good choice. However, this condition is what desired for a particular equipment (coil) performance, data must be checked to verify that the equipment is capable of producing at this condition.
7. A supply condition that falls below the RSHR line can be used, but the room humidity will be lower than the desired design humidity
8 If a supply condition that falls above the RSHR line is used, the room humidity will be higher than the desired design humidity. The diagram below shows the effects of supply conditions which do not fall on the RSHR line

## Slide 49: Room Sensible Heat Ratio (RSHR)
5. Multiple Room Sensible Heat Ratios:
Note that if more than one room (or zone) is conditioned by a single central cooling coil, the coil will normally not be able to simultaneously satisfy the latent loads in all the rooms. This happens because the coil can only operate at a single sensible heat ratio may not be equal to any of the individual room sensible heat ratios.
If it is not possible to satisfy the RSHR condition for all the rooms, one of the following selections must be made:
If control of the room humidity in one of the rooms (or zones) is more critical than the other rooms, the RSHR for that room will establish the design sensible heat ratio and all the other rooms will have humidities that will vary from the desired design condition.
If none of the room humidity requirements are critical, the coil may be selected to satisfy the average humidity requirements of all of the rooms.

## Slide 50: Coil Sensible Heat Ratio (CSHR)
1. Coil Sensible Heat Ratio Without Ventilation (CSHR)
When the HVAC equipment does not include a provision for introducing outdoor air (ventilation) through the cooling coil, the room sensible heat ratio (RSHR) line completely defines all the possible supply air conditions.
In this situation, the sensible and latent loads in the room and on the coil are identical and the room and the coil sensible heat ratio lines are identical.
The room resign condition will be maintained if the supply air condition is located anywhere on the room sensible heat ratio line.
2. Coil Sensible Heat Ratio With Ventilation
When outdoor air is mixed with return air before it passes through the cooling coil, the coil is subject to the room sensible and latent loads and the additional sensible and latent loads that are associated with the outdoor (ventilation) air.
In this case, the ratios of sensible load to total load for the room and for the coil are usually different and the room and the coil sensible heat ratios will be different.

## Slide 51: Coil Sensible Heat Ratio (CSHR) Cont’d

## Slide 52: Coil Sensible Heat Ratio (CSHR) Cont’d

## Slide 53: Coil Sensible Heat Ratio (CSHR) Cont’d
Figure 4.1
Figure 4.2

## Slide 54: Coil Sensible Heat Ratio (CSHR)
3. Construction of the RSHR and CSHR Lines
It is important to understand that the room sensible heat ratio line can always be drawn on the psychrometric chart with complete certainty. This is because the room sensible heat ratio (RSHR) and the room design condition can always be determined from the load calculation information.
However, coil sensible heat ratio (CSHR) is drawn using the following procedure:
Assume water coils can provide leaving air temperatures that are between 15oF and 25oF below the room design temperature at relative humidities between 85% and 95%.
Also assume that DX coils installed in packaged equipment can provide leaving air temperatures which are between 15oF and 20oF below the room temperature at relative humidities between 85% and 95%.
The supply condition of CSHR must fall on the RSHR line
For a packaged DX system, a leaving air DB temperature of 57oF and approximately 90% RH is reasonable.
The following example illustrate how CSHR can be drawn.

## Slide 55: Coil Sensible Heat Ratio (CSHR) Cont’d
Example: Construct the coil sensible heat ratio line using the following information:
Room Sensible Heat = 90,000 Btu/hr
Room Latent = 10,000 Btu/hr
RSHR = 0.90
Room Design = 75oF DB and 50% RH
Outside Design = 95oF DB and 75oF WB
Ventilation Required = 1,000 CFM

## Slide 56: Coil Sensible Heat Ratio (CSHR) Cont’d
Figure 4.4
Fig 4.5

## Slide 57: Coil Sensible Heat Ratio (CSHR) Cont’d

## Slide 58: Coil Sensible Heat Ratio (CSHR) Cont’d

## Slide 59: Coil Bypass Factor & Contact Factor
When air passes across the outside surface of a coil, only part of the air actually contacts the surface and is cooled.
The Bypass Factor (BF) is defined as the proportion of air that does not touch the surface (by-pass air), and is therefore not cooled.
The bypass air is untreated –it leaves the coil at the same conditions as it entered.
Mathematically;
The Contact Factor (CF) is defined as the proportion of air passing through the coil that touches the cooling surface (contact air) and is thus cooled.
It can be assumed that only the air that contacts the cooling surface (contact air) is cooled and dehumidified
Mathematically;
BF + CF = 1 -----> (c)

## Slide 60: Coil Bypass Factor & Contact Factor

## Slide 61: Thermodynamics Laws & Heat Transfer Principles
1st Law of Thermodynamics States that:
Energy In – Energy Out = Change in Store Energy -- (1)
This implies that, energy cannot be destroyed or created but energy can be converted from energy to another.
Example: A hot heating convector in a Hotel room is supplying 4000 Btu/hr of heat. Heat is being transferred from the room air to the outdoor at rate of 6500 Btu/hr. What will happen in the room? What size electric heater should the Hotel manager temporarily use to solve the emergency?

## Slide 62: Thermodynamics Laws & Heat Transfer Principles
1st Law of Thermodynamics emphasizes on:
  Energy Equation to solve problems in HVAC work
  How much energy is used for given task (the power of a pump, the capacity of refrigeration machine)
2nd Law of Thermodynamics States that:
“No machine whose working fluid undergoes a cycle can absorb heat from one system, reject heat to another system and produce no other effect” (Clausius’ Law)
Or 2nd Law of Thermodynamics implies that net heat transfer occurs in the direction of decreasing temperature.
Mathematically;
“No (heat) engine whose working fluid undergoes a cycle can absorb heat from a single reservoir, deliver an equivalent amount of work, and produce no other effect” (Kelvin – Planck).
Analysis of the 2nd Law:
  A heat resource cannot be fully converted to work.
  Refrigeration is a process of moving heat (thermal energy) from a cold region to a warmer region.

## Slide 63: Thermodynamics Laws & Heat Transfer Principles
Example of 2nd Law of Thermodynamics:
An air-conditioned engineered contractor has a choice of using steel or copper piping of the same diameter in chilled water system. Which would be the best choice to minimize energy consumption?
Solution:
Applying 2nd Law of Thermodynamics; Copper tubing has a smoother surface and therefore results less frictional loses. Less energy will be used in the pump, according to the Thermodynamics Second Law.

## Slide 64: Thermodynamics Laws & Heat Transfer Principles
Heat Transfer Principles:
The principles of heat states that, heat will transfer from the warmer body to the cooler body.
There are modes of heat transfer. These include:
  Conduction
  Convection
  Radiation
1. Conduction occurs by direct physical contact between two or more bodies i.e. thermal conduction refers to the direct transfer of energy between particles at the atomic level.
Mathematically:

## Slide 65: Thermodynamics Laws & Heat Transfer Principles
2. Convection occurs by air currents: the thermal convection transfer of energy may include some conduction but refers primarily to energy transfer by eddy mixing and diffusion, i.e., by fluids in motion.
Mathematically;
For a finned-coil fluid-to-air heat exchanger, the general equation for heat transfer is

## Slide 66: Thermodynamics Laws & Heat Transfer Principles
2. Convection transfer cont’d:
For a shell-and-tube fluid-to-fluid heat exchanger, the equation for heat transfer is
3. Radiation occurs by heat rays i.e., thermal radiation describes a complex phenomenon which includes changes in energy form: from internal energy at the source of electromagnetic energy for transmission, then back to the internal energy at the receiver. There is no material medium required for energy transmission, therefore, radiation transfer works best in a perfect vacuum.
Factors that affect radiation heat transfer include:
Emittance
Absorptance
Reflectance
Transmittance
Absolute temperature difference
Geometry

## Slide 67: Thermodynamics Laws & Heat Transfer Principles
3. Radiation heat transfer: One general equation for the net radiant heat transfer between two surfaces is:
Mathematically;

## Slide 68: Estimate of Sensible and Latent Heat Changes
Sensible heat Equation:
Latent Heat Equation:

## Slide 69: Estimate of Sensible and Latent Heat Changes
Example 1: There are 5000 GPM of chilled water being circulated from the refrigeration plant to the air conditioning systems of the buildings at the Refinery Company. The water is cooled from 55oF to 43oF.
Solution:

## Slide 70: Analysis of Thermal Comfort
The purpose of thermal comfort is to provide a comfortable indoor environment, that a person cannot sense a difference between themselves and the surrounding air.
Heating, Ventilating, and air conditioning (HVAC) systems are designed to provide comfort and contain mechanical, pneumatic, electrical, electronic, and chemical components.
HVAC system components include compressors, controls, valves, dampers, actuators, fuels, refrigerants, and blowers.
The most common essentials requirements for comfort are proper temperature setpoints, humidity, circulation, filtration, and ventilation