## Slide 1: Measurement Tools & Verification of Savings Calculations G. Sources of Data and Measurement
Notes: <number>

## Slide 2: G. Sources of Data and Measurement Instruments

## Slide 3: Whole Building
Electric/Natural Gas
1. Monthly bills
2. Time of use meters (large facilities)
3. Smart meters (everyone else)
Smart Meters for Electricity & Natural Gas

## Slide 4: Whole Building
4. Advanced metering or Energy Information systems (EIS)
  a. customer owned, non-revenue grade
  b. System of meters, communication nodes, data storage
  c. User Display Screens

## Slide 5
Typical Architecture of an Energy Information System

## Slide 6: Building Subsystems
Building automation system (BAS)
Metasys (Johnson Controls)
Alerton Technologies
Siemens Building Technologies
Trane
See www.ddc-online.org
Energy Management and Information Systems
PowerLogic ION Enterprise Software
Obvius
others

## Slide 7: Building Subsystems
Typical data available
1. Sub-meters
a. electric
b. BTU meters from central plants
Status/feedback signals (from BAS)
  a. Variable load
  - VFD speed signal
  - inlet guide vane position
  b. Constant Load
  - equipment on/off
A Sub-Meter by Badger Meter Inc.

## Slide 8: Building Subsystems
Sensor data:
a. Ambient temperature (local)
b. Indoor temperature
c. Supply and Return temperatures (water or air)
d. Make sure to check sensor calibration and for gaps or missing values in sensor data

## Slide 9: Weather Data
Websites – NOAA, weather underground
TMY data (from NREL)

## Slide 10: Measurement Devices

## Slide 11: Electrical Metering
M&V Planning <number>
Watts = Amps x Volts x Power Factor
  Power factor is important. For restrictive loads (e.g. incandescent lighting), PF = 1.0 and amps and volts are all that must be measured. For inductive loads, PF must be measured or estimated
  Harmonic distortion may also influence readings
Always measure the true RMS Watts, not simply amps and volts, to include all possible power factor and harmonic influences.
Notes: © Efficiency Valuation Organization
M&V Planning <number>
As a default measure true RMS watts unless you are sure there are no harmonics and no phase shift on the circuit (not just the device being measured).

## Slide 12: Thermal Energy Meters
M&V Planning <number>
Thermal energy meters measure energy rate provided by hot and cold water, often from a central plant to a building.
  Require 2 temperature
  sensors and a flow meter
  Temperature and flow
  sensors may be intrusive
  or surface-mounted
  Sources of error from
  three measurement elements
  Expensive!
Notes: © Efficiency Valuation Organization
M&V Planning <number>
No metering is impossible, just more costly

## Slide 13: Measurement Devices
Data loggers
HOBO
Pace
Dent
Etc.
Outdoor Air Temperature Sensor
4-Channel Data Logger
Electrical Power Logger
HOBOware Pro Data Logger Software
Indoor Temperature Logger

## Slide 14: Measurement Devices
Spot measurement instruments
1. Powersight
2. Fluke Meters
3. Raytek Laser Thermometer
4. Source: PG&E Tool Lending Library
http://www.pge.com/pec/tll/
PowerSight Power Analyzer
Raytek Laser Thermometer