## Slide 1: Measurement Tools & Verification of Savings Calculations F. Application in IPMVP
Notes: <number>

## Slide 2: F. Application in IPMVP
What are the four IPMVP Options for M&V
How do measurement boundaries and savings calculation methods map to IPMVP options?

## Slide 3: IPMVP - Overview
Introduction <number>
Presents a framework and defines terms used in determining ‘savings’ after implementation of a project.
Specifies the topics to be addressed in an M&V Plan for a specific project.
Allows flexibility in creating M&V Plans, while adhering to the principles of: accuracy, completeness, consistency and transparency.
Notes: © Efficiency Valuation Organization
<number>

## Slide 4: IPMVP Options
<number>
Option A. Retrofit Isolation, Key Parameter Measurement
  Savings are determined by field measurement of the key performance parameters which define energy use of affected systems. Parameters not selected for field measurements are estimated.
Option B. Retrofit Isolation: All Parameter Measurement
  Savings are determined by field measurement of the energy use of the affected system.
Option C. Whole Facility
  Savings are determined by measuring energy use at the whole facility or sub-facility level.
Option D. Calibrated Simulation
  Savings are determined through simulation of the energy use of the whole facility or sub-facility. Simulation routines are demonstrated to adequately model actual energy performance measured in the facility.
Notes: IPMVP = International Performance Measurement and Verification Protocol
IPMVP defines four options, which are essentially different combinations of measurement boundaries and savings estimation methods.
There are two retrofit isolation methods, and two whole building (facility) methods
<number>

## Slide 5: Summary of IPMVP Options (I)
<number>
Retrofit Isolation Options
  Option A: Key Parameter Measurement
    Useful with contracts where installation party is responsible for equipment performance but owner responsible for operation hours
  Option B: All Parameter Measurement
    Useful when savings due to EEMs must be known (e.g. EE Programs)
Notes: Retrofit isolation options are used when the savings of individual EEMs need to be verified (or a number of EEMs within a building subsystem)
<number>

## Slide 6: Summary of IPMVP Options (II)
<number>
Whole Building Options
  Option C: Whole Building – Utility Meter Data
    Monthly Data: Useful when savings a large % of annual use (rule of thumb – 15%)
    Interval Data: Can verify smaller savings at whole building level
  Option D: Calibrated Simulation
    Useful when savings large and detailed building model desired
    Projects and investment must be large
Notes: Whole building methods are used when the collective savings of all EEMs within the building must be verified. This includes interactive effects.
Demand response and renewable energy savings are quantified using Option C methods.
<number>

## Slide 7: Mapping Options to Boundaries and Methods
IPMVP Option | Measurement Boundary | Savings Method
Option A | Equipment System | Load and Schedule Calibrated Simulation
Option B | Equipment System | Load and Schedule Regression Method Calibrated Simulation
Option C | Whole Building | Regression Method
Option D | Whole Building | Calibrated Simulation
Notes: <number>