## Slide 1: Measurement Tools & Verification of Savings Calculations E. Savings calculation methods
Notes: <number>

## Slide 2: E. Savings Calculation Methods
What are the main M&V savings calculation methods?
  Load and schedule method
  Regression methods
  Simulations
How are they applied?
What software and tools are available?

## Slide 3: Load and Schedule Method
Based on simple equations:
Variations
  Constant load, constant schedule (hours of use)
    EEM changes hours of use:
    EEM changes load:
  Other equations exist for variable load
Note how ‘adjustments’ are included in calculations:
  EEM changes hours of use – kW same in base and post
  EEM changes load – HRS same in base and post

## Slide 4: Load and Schedule Method
Procedure
  Characterize baseline equipment load and schedule operation
    Constant or Variable
  Determine impact of EEM on load & schedule
    Changes load or changes schedule or both
  Characterize post-install operation
  Define analysis algorithms (pick equation)
  From equation, identify data required
  Develop data collection plan
    Data points (i.e. kW, HRS, etc.)
    Spot measurement
    Monitoring required

## Slide 5: Load and Schedule
Operation Categories
  Four categories are used to characterize the operation characteristics of the end-uses:
    Constant Load, Timed Schedule
    Variable Load, Timed Schedule
    Constant Load, Variable Schedule
    Variable Load, Variable Schedule

## Slide 6: Constant Load, Timed Schedule (CLTS)
Degree of “constant” defined by user
  Variation less than 5% may be OK
Examples
  Lighting under time clock control
  CRAH unit fan 24/7 operation
Notes: A constantly loaded piece of equipment uses a constant kW when operating. There is no change over time.
The equipment may be run by a timer – in which there are a known (or measureable) number of off hours as well as on hours.
CRAH is a ‘computer room air handling unit’ – a fan-coil unit used to keep a data center cool. Typically it runs 24 hrs a day, 7 days a week at constant load (constant kW).
<number>

## Slide 7: Variable Load, Timed Schedule (VLTS)
kW varies with load
  kW varies based on cfm, ton, speed, etc.
Total hours constant, distributed over several load bins
Examples
  WW treatment blowers maintaining constant DO levels (24/7)
  CRAC unit operation (split system, condenser on roof)
Notes: The load in variable load equipment changes with some other parameter, such as airflow, cooling capacity, or motor speed. There is a mathematical relationship between kW and the load-driving parameter.
The amount of time the equipment spends at any one time is represented by a load frequency distribution. The chart shows an example of an LFD. Loads are ‘binned’ into increments of 20% up to 100%, and the total hours of use are still constant.
cfm – cubic feet per minute – a unit of airflow
ton – a capacity for cooling – wiki definition is: A ton of refrigeration (commonly abbreviated as RT) is a unit of power used in some countries (especially in North America) to describe the heat-extraction capacity of refrigeration and air conditioning equipment. It is defined as the heat of fusion absorbed by melting 1 short ton (0.893 long ton; 0.907 t) of pure ice at 0 °C (32 °F) in 24 hours.[1][2] It is equivalent to the consumption of one ton of ice per day and originated during the transition from stored natural ice to mechanical refrigeration.
speed – as in motor speed, which may be modulated by a variable frequency drive. kW draw of the motor changes as the motor speed changes.
<number>

## Slide 8: Constant Load, Variable Schedule
Load is constant, but unknown hours-of-use
Examples:
  Lighting controlled with occupancy sensors
  Constant speed cooling tower fans – hours vary with ambient temperature

## Slide 9: Variable Load, Variable Schedule
Hours-of-use in each bin and total are unknown
Examples
  Chilled water system maintaining CHWST reset schedule
  Industrial VFD compressed air system

## Slide 10: Load and Schedule: Algorithm
Identify baseline operation category
Determine impact of EEM
  Changes load, changes schedule
  Changes load or schedule from constant to variable
Based on EEM impact, identify post-installation operation category
Select equation, define analysis procedure
Determine relationships between load & hours-of-use, and other parameters
  e.g. T, cfm, gpm, speed, tons, etc.
Collect baseline and post-install data
Calculate savings

## Slide 11: Load and Schedule - Applicability
Loads that may be isolated and measured
  Air or water flow, heating Btu/h, cooling tons, etc.
  Relationship to kW known or may be developed
Energy flows: there should be few and straightforward to measure
There are negligible or ignorable interactive effects with other equipment

## Slide 12: Equations
Savings equation selected based on
  Characteristics of equipment operation
  Impact of ECM
Select equation to minimize data requirements
  e.g. lighting fixture replacement, constant hours-of-use
    Measure kW in baseline period (not hours-of-use)
    Measure kW and hours-of-use in post-install period

## Slide 13: Equations – Examples
CLTS
  Changes load
  Changes hours-of-use
  Changes load from constant to variable
  Changes hours-of-use from constant to variable

## Slide 14: Equations – Examples, cont.
VLTS
  Changes load
  Changes hours-of-use
  Changes hours-of-use from constant to variable

## Slide 15: Equations – Examples, cont.
CLVS
  Changes load
  (or )
  Changes hours-of-use
  Changes load from constant to variable

## Slide 16: Equations – Examples, cont.
VLVS
  Changes load
  Changes hours-of-use
  Changes load and hours-of-use

## Slide 17: Simple Example
A storage building at an Army Base is undergoing a lighting retrofit. The existing exterior lighting of the building consists of (9) 70W Metal Halide Wall pack fixtures.
The following procedure complies with load and schedule approach and is used to determine project energy savings
Step1. – The existing fixtures produce a constant wattage and were observed to operate continuously day or night. Therefore the Constant Load Timed Schedule (CLTS) category best represents this existing equipment’s load and hours-of-use characteristics.
Step2. – The ECM includes retrofitting the (9) 70W Metal Halide Wall pack fixtures with (9) 36W LED Wall pack fixtures and installing Daylight controls as shown in Table 1 and Table 2

## Slide 18: Example, cont.
Fixture | kW/Fixture | Qty | Hours of operation | Total kW
70W Metal Halide Wall pack | 0.095 | 9 | 8,760 | 0.855
Fixture | kW/Fixture | Qty | Hours of operation (estimated) | Total kW
36W LED Wall Pack | 0.036 | 9 | 4,380 | 0.324
Table 1
Table 2

## Slide 19: Example, conclusion
Step 3. This ECM will reduce the equipment’s load and hours of operation. The anticipated post-installation equipment’s load and hours of use characteristics best fit into the CLVS category. Therefore, the appropriate equation to use in determining savings is:
  kWh saved = kW existing x HRS existing– kW proposed x ∑HRS proposed
In review, the key parameters estimated were load and hours of use. Data sources for those parameters included nameplate information (in this case, the lamp label or model number), A Table of Standard Wattages, interviews with the facilities staff and a light logger.
Total savings for this project were 6,071 kWh.
Notes: The table of standard wattages for this example were found on:
<number>

## Slide 20: Advantages of L&S Method
M&V is extension of methods used to calculate ex-ante savings
Allows use of technical (not measured) info.
Many required measurements may be cost-effectively obtained
Can apply to more complicated systems, if operation characteristics same
Can quantify savings uncertainty, if required

## Slide 21: Disadvantages
Not practical for multiple EEMs throughout a facility
Does not account for savings interactions
  e.g. cooling savings from a lighting retrofit
Not well applied to end-uses with highly random load and schedule characteristics

## Slide 22: Regression Method
Empirical relationships between energy use and factors that influence energy use
  Ambient temperature
  Time (of year, of week, etc.)
  Occupancy
  Etc.
Influencing parameters must be measureable
Notes: Measurable requirement often eliminates occupancy.
<number>

## Slide 23: Regression Method
General procedure
  Develop a regression relationship between energy use and one or more independent variables using data from the baseline period
  Check model quality – fit statistics, error
  Using post-install data, determine ‘adjusted baseline’ in post-install period
  Subtract actual energy use to determine savings (avoided energy use)

## Slide 24: Monthly Bill Regression - Heating
Based on monthly energy bills
Calculate heating degree-days to determine the weather-induced load on the heating system
  Requires a balance-point temperature, which is the temperature above which the building requires heating, and varies from building to building, typically 60 or 65F.
  (toss out negative values)
Notes: Note that the calculation relies on an ambient temperature, and an average of the hourly temperatures is used.
A more accurate regression can be made using the hourly data, HDH – heating degree-hours. This allows a count of the number of hours heating is needed in a building, not just days. This generally is more accurate in temperate climates where temperatures vary above and below Tbal throughout the day.
Ask the class if we are in a temperate climate (yes).
<number>

## Slide 25: Monthly Bill Regression - Cooling

## Slide 26: Weather Data
The NOAA website and other websites such as weather underground provide weather data including ambient dry-bulb temperature for many airports and other weather stations throughout the country.
  www.noaa.gov
  www.wunderground.com
Values provided are generally on an hourly basis.
Data must be checked, often there are gaps and erroneous values in the data
Some site provide heating degree days directly
  www.degreedays.net

## Slide 27: Monthly Bill Regressions
Most spreadsheet tools have a regression tool.
Tabulate the monthly bills and HDD for each month in a spreadsheet.
Also record the number of days each month.
Use the regression tool to determine the linear regression’s model coefficients and coefficient of determination (R2)
Also calculate the CV(RMSE) – coefficient of variation of the root mean squared error
Notes: R2 and CV(RMSE) are generally accepted model “fit statistics”.
Ei is the measured data, Ei “hat” is the predicted data from the model, n is the total number of data points in the set, p is the number of parameters (coefficients) in the model. For example, a simple linear equation: y=a*x + b has 2 parameters (a and b). E “bar” is the average energy use over all the measured Ei points.
R2 should generally be higher than 0.8, and CV should be low, < 10% is ideal.
<number>

## Slide 28: Monthly Bill Regression: Brief Example
<number>
Monthly Gas Bill Data (cu.ft.)
Notes: The gas bills (in cubic feet) for each month of the year are tabulated. Use a spreadsheet with a linear regression function. The bill date, and number of days should be included in the tabulation.
Find a local weather station, download the weather, and calculate the number of HDD (or HDH) for each month.
Use the spreadsheet’s regression tool to determine the predicted gas consumption (shown in last column). Use the “ANOVA” (analysis of variance) table in Excel to find the model coefficients and coefficient of determination (R2). Calculate the CV(RMSE) – coefficient of variation of the root mean squared error (
In this example, the problem is carried out incorrectly on purpose. Later the correction will be made. But it’s a good time to ask the class if they know what the error is.
<number>

## Slide 29: Baseline Model Improvement
<number>
Improve example linear model by:
  Normalizing the data (divide Gas and HDD by no. days)
  This “weights” the points by the number of days
Perform regression on weighted values
  Result: Gas = Days*(3,651+177*HDDPD)
  NBE = -0.044% (was 0.8%)

## Slide 30: Baseline Model: Actual v. Predicted
<number>
Gas Use = Days*(3,651+177*HDDPD)
R2 = 0.92, CV(RMSE) = 8.9%
Notes: Check the
<number>

## Slide 31: Adding Post-Installation Data
<number>
Notes: <number>

## Slide 32: Baseline Projection & Savings
<number>
Post-Installation Period Savings: 609,567 cu.ft. ± 17%
Savings percentage: 32%

## Slide 33: Best Applications with Monthly Data
<number>
Significant energy savings
  Rule of thumb: 10-15% or more of consumption measured by the utility meter
All parameters which significantly affect energy usage can be clearly identified (during baseline and after implementation)
Adjustment factors are simple
Individual ECM measurement is not required
Multiple ECMs
Complex ECMs

## Slide 34: Energy Models based on Interval Data
“Interval data” = data from Time-of-Use Meters, typically in very large commercial and industrial buildings.
Smart Meters in smaller buildings and houses are now providing interval data.
Interval data is energy use data from short time interval measurements, typically 15-minutes for electricity.

## Slide 35: Short Time Interval Methods
<number>
Dependency on ambient temperature
Dependency on day of week
T
kW
Notes: Interval data provides
-more detailed insight into energy use patterns
-faster feedback on energy use
Chart shows that energy use has a dependency on ambient temperature as well as day of week
<number>

## Slide 36: M&V with Interval Data
Notes: The M&V procedure is similar to that using monthly billing data.
-make a model with baseline period data
-determine adjusted baseline in post-installation period
-subtract measured post-install energy from adjusted baseline to determine savings
There are a lot more points available (i.e. hourly or daily, rather than monthly).
Analysis is more complicated, as more advanced regression techniques are used.
<number>

## Slide 37: Useful Software
<number>
ASHRAE Inverse Modeling Toolkit (RP1050)
  Purchase with Research Project 1050
Energy Explorer
  “Change-point” models
  Source: Prof. Kelly Kissock, University of Dayton
Energy Charting and Metrics Tool
  www.northwrite.com
PG&E Universal Translator M&V Analysis Module
  www.utonline.org (coming soon)

## Slide 38: Calibrated Simulation
A simulation of a building or system is made using a recognized software
  eQUEST
  EnergyPlus
  EnergyPRO
The building or system is ‘modeled’ within the software, and ‘calibrated’ with measured data from the building to make sure the model accurately predicts baseline energy use
After EEMs are installed, the simulation is run with post-installation data (temperature, occupancy, etc.) to determine the adjusted baseline.
Savings are determined by subtraction of the measured post-installation use from the adjusted baseline.
Notes: Calibrating a simulation model requires specialized skill and experience, requires much measured data, and requires that the simulation be able to model poor building operations well.
This method is highly technical and is only recommended for projects where there is the necessary skills and experience.
<number>

## Slide 39: Calibrated Simulation
Advantages
  Can quantify individual EEM savings as well as whole building
  Useful to have a simulation for other purposes
Disadvantages
  Can be most difficult and expensive method
  Requires a lot of building data to calibrate
  Simulation programs may model the building well