## Slide 1: Measurement Tools & Verification of Savings Calculations B. Definitions and Concepts
Notes: <number>

## Slide 2: B. Definitions and Concepts
What is the common M&V terminology?
What are its core concepts?

## Slide 3: Definitions
Avoided energy use
  The reduction in energy use in the period after EEMs are installed. It is the difference in energy use the building or system would have used and the amount it actually used in the post-install period
Normalized savings
  The amount of savings that would have been achieved had the facility or equipment operated under another set of conditions other than the post-installation period. Both baseline and post-installation energy use are normalized to another set of conditions – such as long term average weather conditions

## Slide 4: Definitions, cont.
Adjustments to energy use
  Adjustments are made to either baseline or post-installation energy use to assure a fair calculation of savings, and that savings are due to the installed EEMs, an not due to weather, changes in occupancy, and so on.
Energy Efficiency Measure (EEM)
  An EEM improves the energy utilization of equipment or systems within a facility. It may be one or multiple improvements at a time.
Notes: Throughout this course, we refer to EEMs – energy efficiency measures. Note that the process of M&V is the same whether for energy conservation measures (ECMs) or renewable energy projects.
It is also the same for demand response measures, but the baseline and post-installation time period is much shorter – days, not years.
<number>

## Slide 5: Definitions, cont.
Baseline Energy
  The energy use occurring during the baseline period without adjustments (IPMVP def.)
Baseline period
  The period of time chosen to represent the operation of the facility or systems prior to the implementation of an EEM. Typically the baseline period includes a full cycle of operation when energy use is influenced by various conditions

## Slide 6: Definitions, cont.
Measurement Boundary
  An imaginary boundary drawn around equipment or systems of interest in the analysis. Such boundaries may include the whole facility, specific affected systems, or specific affected equipment. All energy uses within the measurement boundary must be measured or reliably estimated
Interactive effects
  Energy savings or penalties created by an EEM but not measured within the measurement boundary

## Slide 7: Ex-Ante Savings Estimates
Audit requirement, provides owner with critical information on which EEMs to implement
  Which EEMs provide most savings
  Which EEMs are most cost effective
  Etc.
Provides basis of long-term energy management plan
However…

## Slide 8: Savings Can Only Be Estimated
Energy savings cannot be measured because they are the absence of energy use. Savings can only be estimated.
Audit savings estimations:
  These are “ex-ante” meaning estimated prior to implementing any project
    No before-after comparison possible
    Such estimates require assumptions about energy use/equipment performance after the EEMs are installed
  Audit economics and facility access may dictate use of rough estimation methods, ‘deemed’ savings, little site data
  Even the most thorough, data-driven analysis may be in error because no one can predict the future
  Uncertainty analysis typically not performed on ex-ante estimations – no way to understand risk

## Slide 9: EEMs May be Installed Incorrectly
Savings estimates may be correct, but:
  the wrong equipment may be installed
  equipment may be installed incompletely or incorrectly,
  controls may be incorrectly programmed
  the equipment is not properly commissioned
  and so on

## Slide 10: EEMs May be Defeated Quickly
Operators may lack training on how to operate the new equipment
Comfort complaints may cause operators to improperly operate equipment or revert to baseline practices
  Example: daylight sensors may dim lights, still providing required light levels, but occupants unused to new lighting effect complain. Operator overrides daylight dimming controls.

## Slide 11: Savings Quality Assurance Needed
Methods:
  “Sanity check” such as checking the percent savings versus the total energy use of system or facility
  Alternate savings calculations – savings may be estimated using a completely different method
  Peer Review of savings estimates, data and method. Checks for proper application of principles, correct data, correct interpretations and assumptions
  Correcting ex-ante savings estimates with post-install data – verifies assumptions on how systems and equipment performs post-installation
  Measurement and verification (M&V) – using energy use measurements before and after installation, adjusting to same conditions, and estimating savings
Notes: These are listed in order from least to most rigorous, with industry standard M&V methods as the most rigorous.
Costs for these methods do not necessarily increase with the level of rigor, although the least rigorous is usually the least costly
<number>

## Slide 12: Industry Standard M&V
International Performance Measurement and Verification Protocol
  Internationally recognized standard
  Started in US to develop guidelines for savings for ESCO contracts
  www.evo-world.org
American Society of Heating Refrigeration and Air-conditioning Engineers (ASHRAE) Guideline 14-2002 Measurement of Energy and Demand Savings
  www.ashrae.org
Notes: IPMVP is the more flexible, more general document. It describes adherence requirements. Its terminology and framework provide the background for this course.
ASHRAE Guideline 14 is very rigorous and requires savings to be stated with an estimate of savings uncertainty. It is a compliance standard (i.e. savings is compliant to ASHRAE Guideline 14 if the savings can be stated within 50% precision at 68% confidence level)
<number>

## Slide 13: Practical Guidelines
Several Exist:
  Guidelines for Verifying Existing Building Commissioning Project Savings
    www.cacx.org California Commissioning Collaborative
    4 methods:
      Engineering calculations with verification
      End-use metering
      Energy modeling using interval data
      Computer simulation
  Federal Energy Management Program M&V Protocol
  www.ateam.lbnl.gov

## Slide 14: Practical Guidelines
Bonneville Power Administration
  Practical guidance for verifying savings for retrofits, EBCx, in multiple sectors
  www.conduitnw.org
  Various guides and guidelines:
    Verification by Equipment or End-Use Metering
    Verification by Energy Modeling
    Regression Guide
    Sampling Guide

## Slide 15: IPMVP M&V
Fundamental concept:
  Relies on direct measurements of energy use before and after EEMs are installed in a system or facility.
Baseline or post-installation (or both) energy use is adjusted to the same set of conditions, before calculating savings
Notes: Note the subtle difference with the next-most rigorous verification method on slide 21: ex-ante savings estimates are made using operational data and physical properties and relationships to determine energy use of the systems, component of system. While some direct energy measurements are made, these engineering calculations rely on non-energy measurements, therefore they are not IPMVP-adherent
<number>

## Slide 16: IPMVP Requirements – 2 parts
Operational Verification
  Verify potential to perform (commissioning)
    ECMs are installed correctly
    Operate correctly
    Have potential to generate savings
2) Savings Verification
- Quantify actual savings

## Slide 17: IPMVP Requirements
One-time visual inspection & review of contractor invoices
Spot measurements of key operational parameters
One time collection and analysis of short term trends of key operational parameters
Functional testing of system operations, monitoring and analysis of operational parameters under all expected conditions
Most Rigorous
Least Rigorous
Operational Verification
A “sanity check” on the percentage of savings from annual usage totals
Comparison of results from an alternate savings calculation
Peer review of savings calculations and use of collected post-installation data to correct them
Savings determined from baseline or post-installation model development and projection to the same set of conditions (IPMVP)
Most Rigorous
Least Rigorous
Savings Verification
Notes: There are two key components of M&V: operational verification and savings verification.
Operational verification: verifies an EEM’s potential to generate savings . It can be applied with various levels of rigor, as the chart shows.
Savings verification: accounts for the amount of savings actually achieved. It may also be applied with increasing levels of rigor, with the most rigorous methods being adherent with IPMVP principles.
<number>