## Slide 1: Measurement Tools & Verification of Savings Calculations D. Measurement Boundary
Notes: <number>

## Slide 2: D. Measurement Boundary
Imaginary boundary around a building, a system, or a piece of equipment
  EEM affects energy consumption within measurement boundary
  Must account for all energy across the boundary
Measurement boundaries are selected based on
  Number of EEMs
  Number of systems affected by the EEMs
  Amount of savings
  Availability of data / potential to obtain data
  Goals of project
Notes: <number>

## Slide 3: Measurement Boundary
Whole Building
  Includes all systems
    Good when multiple systems affected
  Relatively few data sources:
    Main utility meters (gas and electric)
    Local weather data
  Savings must be large (> 10%)
  Includes
    Interactive effects
    All other effects
<number>

## Slide 4: Measurement Boundary
<number>
Building subsystem (HVAC)
  Chiller, CHWP, CT, CWP, HWP, Supply & Return fans
  Multiple data points needed:
    kW or status on each component
    Sources: EMS trend logs, data loggers, submeters
  Savings must be large only in relation to annual system energy use
  Only accounts for savings within system

## Slide 5: Measurement Boundary
Equipment
  e.g. Chiller only, pump only, lighting, etc.
  Few data points
    Supply, return water temps, flow
    Chiller kW, OAT
  Savings for equipment only

## Slide 6: Convenient Boundary Definitions
By California End-Use Survey End-Use Categories
  Reference: http://www.energy.ca.gov/ceus
HVAC
Space Heating
Space Cooling
Ventilation
Non-HVAC
Cooking
Refrigeration
Air Compressors
Domestic Water Heating
Inside Lighting
Outdoor Lighting
Office Equipment
Miscellaneous Equipment
Motors

## Slide 7: System Boundary by ‘Service Provided’
Chilled water system:
  Chiller, CHW pumps, etc.
Air handling system:
  Supply fan, return fan, exhaust fan
Hot water system:
  Boiler, HW pumps