## Slide 1: Chapter Ten
Program Control Instructions
Notes: <number>

## Slide 2: Objectives
Write a program using a latching relay
Understand the term retentive
Write a program using a master control relay
Understand the importance of a safety circuit
Notes: <number>

## Slide 3: Objectives (cont’d.)
Write a program using the jump and label instructions
Give a reason for using the temporary end instruction
Notes: <number>

## Slide 4: Master Control Relay Instructions
Master control
  Often used to control power
    To entire circuit
    Or to selected rungs
  Circuit (or selected rungs) can be deenergized by turning off master control relay
Notes: <number>

## Slide 5
Figure 10-1 Hard-wired master control relay
Notes: <number>

## Slide 6: Master Control Relay Instructions (cont’d.)
MCRs often used with circuits with off-delay timers
  Circuit can be shut down without waiting for timers to time out
Master Control Resets
  Alternate name for Master Control Relays
  Reset output to zero or OFF
Notes: <number>

## Slide 7: Allen-Bradley SLC 500 and MicroLogix MCR Instruction
Refer to Figure 10-2
  When MCR instruction is true:
    Outputs in rungs that follow are controlled by logic programmed for each rung
  When MCR instruction is false:
    Rungs below the MCR are false and cannot energize
    Exception: latching relay instruction will remain true
Notes: <number>

## Slide 8
Figure 10-2 Allen-Bradley MCR Instruction
Notes: <number>

## Slide 9
Figure 10-3 Two MCR instructions used to create a control zone
Notes: <number>

## Slide 10: Latching Relay Instructions
Traditional hard-wired latching relays
  Used when contacts must remain open or closed
    Even though coil is energized only a short time
  Two coils used: latch and unlatch
  Mechanical linkage holds relay in closed position
Notes: <number>

## Slide 11
Figure 10-4 Mechanical latching relay
Notes: <number>

## Slide 12: Latching Relay Instructions (cont’d.)
Programming can replace mechanical latching relays
  Perform logic of an actual latching relay
Programmed instructions are retentive during a power failure
  State of latch instruction retained in memory
Notes: <number>

## Slide 13
Figure 10-5 Programmed latch and unlatch rungs
Notes: <number>

## Slide 14: Safety Circuit
Figure 10-6 Safety circuit
Notes: <number>

## Slide 15: Jump and Label Instructions
Allow for skipping over portions of program
  Saves scan time
Jump instruction
  Tells processor to jump over a portion of the program
  Label instruction tells where to jump to
Notes: <number>

## Slide 16
Figure 10-7 Programming the Jump (JMP) and Label (LBL) instructions
Notes: <number>

## Slide 17: Jump to Subroutine, Subroutine, and Return Instructions
Subroutines
  Used to organize program
  Blocks of programming logic that can be reused
Instructions differ widely among PLC manufacturers
Notes: <number>

## Slide 18: Temporary End Instruction
Instructs processor to stop scanning at a certain point
Used for debugging
Notes: <number>

## Slide 19
Figure 10-9 Allen-Bradley PLC – Temporary End Instruction (TND)
Notes: <number>

## Slide 20: Always False Instruction
Used when debugging
Rung will always be false
Figure 10-10 Always False Instruction (AFI)
Notes: <number>

## Slide 21: One-Shot Instruction
Makes rung true for just one program scan
Figure 10-11 One-Shot Instruction
Notes: <number>

## Slide 22: Summary
Latching and master control instructions can be programmed to act like real-world counterparts
Safety circuit should be added when personnel are involved
Various PLC instructions can be used to perform different program tasks
Notes: <number>