## Slide 1: Chapter Nine
Programming Considerations
Notes: <number>

## Slide 2: Objectives
Define a network
Describe the term dummy relay
Understand the horizontal and vertical contact limits
Define the term nesting
Correctly wire and program STOP buttons
Notes: <number>

## Slide 3: Objectives (cont’d.)
Describe the difference between logical and discrete holding contacts
Notes: <number>

## Slide 4: Network Limitations
Network
  Group of connected logic elements that perform a specific function
Some PLCs have limitations
  Number of logic symbols included on the horizontal line
  Number of parallel lines in a network
  Number of outputs per network
Notes: <number>

## Slide 5
Figure 9-2 Network limits
Notes: <number>

## Slide 6: Network Limitations (cont’d.)
Size of user memory
  Limits number of networks or rungs
When circuit requires more contacts than network allows:
  Contacts split into two rungs
  First rung programmed to dummy relay
  Address of dummy relay is address of first N.O. contact on second rung
Notes: <number>

## Slide 7
Figure 9-4 Parallel contacts split into two rungs (networks)
Notes: <number>

## Slide 8
Figure 9-5 Parallel output format
Figure 9-6 Multiple outputs
Notes: <number>

## Slide 9: Programming Restrictions
PLC does not allow programming vertical contacts
Figure 9-7 Vertical contacts
Notes: <number>

## Slide 10: Programming Restrictions (cont’d.)
Figure 9-9 Equivalent circuit without vertical contacts
Notes: <number>

## Slide 11: Programming Restrictions (cont’d.)
Flow of power is from left to right only
  And vertically up or down
Figure 9-10 Hard-wired circuit
Notes: <number>

## Slide 12
Figure 9-11b Circuit properly programmed
Figure 9-11a Circuit improperly programmed
Notes: <number>

## Slide 13: Programming Restrictions (cont’d.)
Some PLCs do not allow nesting of contacts
Figure 9-12a Nested contacts
Notes: <number>

## Slide 14: Programming Restrictions (cont’d.)
Figure 9-12b Programmed to eliminate nested contacts
Notes: <number>

## Slide 15: Program Scanning
PLC scanning methods
  Left to right, top to bottom
Figure 9-16 One scan turns on L3
Figure 9-17 Three scans required to turn on L3
Notes: <number>

## Slide 16: Programming STOP Buttons
Wiring STOP buttons in N.O. position
  Common during the 1980s
  Safety hazard
All STOP buttons must be wired:
  So switch failure or broken wire will break continuity and turn circuit OFF
Notes: <number>

## Slide 17: Logical Holding Instructions
Previous programming examples
  Output address used to address holding contacts
  Eliminates need to wiring holding contacts on motor starter
Notes: <number>

## Slide 18: Logical Holding Instructions (cont’d.)
When output address used for holding contacts (logic):
  Circuit maintained logically because output point turned ON
  No guarantee actual motor starter has been energized
Notes: <number>

## Slide 19: Discrete Holding Contacts
Wire holding contacts of motor starter to input module point
  Use that address when programming holding contacts
  Will know starter is actually energized
Notes: <number>

## Slide 20: Overload Contacts
Common practice
  Do not wire overload contacts to input module
  Wire in series with starter coil
Motor overload that opens the overload contacts:
  Also opens starter coil circuit
Notes: <number>

## Slide 21
Figure 9-19 Overload contacts wired in series with the starter coil
Notes: <number>

## Slide 22: Summary
Each PLC has maximum network size
  Limits number of horizontal and vertical contacts per rung
Memory size limits the number of rungs
Process reads logic from left to right only
  And vertically either up or down
Some PLCs do not allow nested contacts
Notes: <number>