## Slide 1: Chapter 7
Solenoids
Section 7-1 Electromagnets
Section 7-2 Solenoids
Section 7-3 Solenoid Characteristics
Section 7-4 Solenoid Applications
Section 7-5 Troubleshooting Solenoids
Notes: Chapter 7-<number>

## Slide 2: Objectives Section 7-1 Electromagnets
Define electromagnet and explain the left-hand rule.
State the main characteristics of electromagnets.
Notes: Chapter 7-<number>

## Slide 3
The left-hand rule states that if the fingers of the left hand are wrapped in the direction of the current flow in a coil, the left thumb points to the magnetic north pole of the coil.
Notes: An electromagnet consists of an iron core inserted into a coil. The iron core concentrates the lines of force produced by the coil. With the core in place and the coil energized, the polarity of the magnet can be determined using the left-hand rule. The left-hand rule states that if the fingers of the left hand are wrapped in the direction of the current flow in a coil, the left thumb points to the magnetic north pole of the coil. See Figure 7-1.
Chapter 7-<number>

## Slide 4: 7-1 Checkpoint
Does the added iron core of an electromagnet increase or decrease the magnetic lines of force?
In an electromagnet, what determines the strength of the magnetic field?
What is the left-hand rule used to determine when the direction of current flow is known?
Notes: Chapter 7-<number>

## Slide 5: Objectives Section 7-2 Solenoids
Define solenoid and state the function of each part used to produce linear motion in a solenoid.
Understand why solenoids are available in different operating configurations to meet different application requirements.
Describe the construction of a solenoid.
Notes: Chapter 7-<number>

## Slide 6
The five solenoid configurations are clapper, bell-crank, horizontal-action, vertical-action, and plunger solenoids.
Notes: Solenoids are configured in various ways for different applications and operating characteristics. The five solenoid configurations are clapper, bell-crank, horizontal-action, vertical-action, and plunger. See Figure 7-2.
Chapter 7-<number>

## Slide 7
In a plunger solenoid, a spring is used to move the rod a short distance from its center in the coil. The rod moves against the spring tension to recenter itself when the current is turned on.
Notes: A plunger solenoid contains only a movable iron cylinder, or rod. A movable iron rod placed within the electrical coil tends to equalize or align itself within the coil when current passes through the coil. The current causes the rod to center itself so that the rod ends line up with the ends of the solenoid if the rod and solenoid are of equal length. In a plunger solenoid, a spring is used to move the rod a short distance from its center in the coil. The rod moves against the spring tension to recenter itself in the coil when the current is turned on. The spring returns the rod to its off-center position when the current is turned off. The motion of the rod is used to operate any number of mechanical devices. See Figure 7-3.
Chapter 7-<number>

## Slide 8
In AC solenoids, the magnetic assembly and armature consist of a number of thin pieces of metal laminated together.
Notes: Eddy current is unwanted current induced in the metal structure of a device due to the rate of change in the induced magnetic field. Strong eddy currents are generated in solid metal when used with alternating current. In AC solenoids, the magnetic assembly and armature consist of a number of thin pieces of metal laminated together. The thin pieces of metal reduce the eddy current produced in the metal. See Figure 7-4. Eddy current is confined to each lamination, thus reducing the intensity of the magnetic effect and subsequent heat buildup. For DC solenoids, a solid core is acceptable because the current is in one direction and continuous.
Chapter 7-<number>

## Slide 9
A small air gap is left in the magnetic laminate assembly to break the magnetic field and allow the armature to drop away freely after being de-energized.
Notes: As the coil is de-energized, some magnetic lines of force (residual magnetism) are always retained and could be enough to hold the armature in the sealed position. To eliminate this possibility, a small air gap is always left between the armature and the magnetic laminate assembly to break the magnetic field and allow the armature to drop away freely when de-energized. See Figure 7-5.
Chapter 7-<number>

## Slide 10
A shading coil sets up an auxiliary magnetic field that helps hold in the armature as the main coil magnetic field drops to zero in an AC circuit.
Notes: A shading coil is a single turn of conducting material (normally copper or aluminum) mounted on the face of the magnetic laminate assembly or armature. See Figure 7-6. A shading coil sets up an auxiliary magnetic field that helps hold in the armature as the main coil magnetic field drops to zero in an AC circuit.
Chapter 7-<number>

## Slide 11: 7-2 Checkpoint
What is the movable part of a solenoid called?
Why are solenoid armatures laminated?
Why is a shading coil added to the armature of a solenoid?
Notes: Chapter 7-<number>

## Slide 12: Objectives Section 7-3 Solenoid Characteristics
State common problems, such as inrush current, that solenoids produce in the electrical system.
Describe the solenoid selection methods.
Notes: Chapter 7-<number>

## Slide 13
The mechanical life of most coils is extended by encapsulating the coil in an epoxy resin or glass-reinforced alkyd material.
Notes: Magnetic coils are normally constructed of many turns of insulated copper wire wound on a spool. The mechanical life of most coils is extended by encapsulating the coil in an epoxy resin or glass-reinforced alkyd material. See Figure 7-7. In addition to increasing mechanical strength, these materials greatly increase the moisture resistance of the magnetic coil. Because magnetic coils are encapsulated and cannot be repaired, they must be replaced when they fail.
Chapter 7-<number>

## Slide 14
Solenoid inrush current is approximately 6 to 10 times the sealed current.
Notes: Solenoid coils draw more current when first energized than the amount that is required to keep them running. In a solenoid coil, the inrush current is approximately 6 to 10 times the sealed current. See Figure 7-8. After the solenoid has been energized for some time, the coil becomes hot, causing the coil current to fall and stabilize at approximately 80% of its value when cold. The reason for such a high inrush current is that the basic opposition to current flow when a solenoid is energized is only the resistance of the copper coil. Upon energizing, however, the armature begins to move iron into the core of the coil. The large amount of iron in the magnetic circuit increases the magnetic opposition of the coil and decreases the current through the coil. This magnetic opposition is referred to as inductive reactance or total impedance. The heat produced by the coil further reduces current flow because the resistance of copper wire increases when hot, which limits some current flow.
Chapter 7-<number>

## Slide 15
Manufacturers provide letter or number codes to indicate the solenoid mount.
Notes: Manufacturers provide letter or number codes to indicate the solenoid mount. See Figure 7-9. For example, an A solenoid is selected for a door latch application because the door latch application requires an end-mounting solenoid.
Chapter 7-<number>

## Slide 16
Manufacturers provide letter or number codes to indicate the voltages that are available for a given solenoid.
Notes: Manufacturers provide letter or number codes to indicate the voltages that are available for a given solenoid. See Figure 7-10. For example, a 2 A solenoid may be used for an application that requires a 115 V coil.
Chapter 7-<number>

## Slide 17: 7-3 Checkpoint
What is the initial current draw of a solenoid called?
What is the operating current of a solenoid called?
If the voltage applied to a solenoid is higher than the rating of the solenoid, will the current draw increase or decrease?
What is the number of times a solenoid can operate in a given time period (usually operations per minute) called?
Notes: Chapter 7-<number>

## Slide 18: Objectives Section 7-4 Solenoid Applications
State the number of positions, number of ways, and type of actuator a directional control valve has.
List the different types of systems and applications solenoids may be used for.
Notes: Chapter 7-<number>

## Slide 19
Positions are the number of locations within the valve in which the spool can be placed to direct fluid through the valve.
Notes: A manual directional control valve is placed in different positions to start, stop, or change the direction of fluid flow. See Figure 7-11. A position is the number of locations within the valve in which the spool can be placed to direct fluid through the valve. A directional control valve normally has two or three positions.
Chapter 7-<number>

## Slide 20
A way is a flow path through a valve.
Notes: A way is a flow path through a valve. Most directional control valves are either two-way or three-way valves. The number of ways required depends on the application. Two-way directional control valves have two main ports that allow or stop the flow of fluid. Two-way valves are used as shutoff, check, and quick-exhaust valves. See Figure 7-12.
Chapter 7-<number>

## Slide 21
In an electrical control valve, the solenoid acts as the actuator.
Notes: A manual directional control valve uses a handle to change the valve spool position. An electrical control valve uses an actuator to change the position of a valve spool. In an electrical control valve, the solenoid acts as the actuator. See Figure 7-13.
Chapter 7-<number>

## Slide 22
In a refrigeration system, direct-acting two-way valves may be constructed as normally open (NO), where the valve is open when de-energized and closed when energized; or they may be constructed as normally closed (NC), where the valve is closed when de-energized and open when energized.
Notes: Direct-acting, two-way valves are commonly used in a refrigeration system. Two-way (shutoff) valves have one inlet and one outlet pipe connection. These units may be constructed as normally open (NO), where the valve is open when de-energized and closed when energized; or they may be constructed as normally closed (NC), where the valve is closed when de-energized and open when energized. See Figure 7-14.
Chapter 7-<number>

## Slide 23
Refrigeration systems may use different solenoids, such as liquid line solenoids and hot gas solenoids.
Notes: A number of different solenoids may be used in a typical refrigeration system. The liquid line solenoid valves could be operated by two-wire or three-wire thermostats. The hot gas solenoid valve remains closed until the defrost cycle and then feeds the evaporator with hot gas for the defrost operation. See Figure 7-15.
Chapter 7-<number>

## Slide 24
Different solenoids are used for the safe operation of an oil-fired single-burner system.
Notes: Solenoids may also be used in an oil-fired single-burner system. See Figure 7-16. The solenoids are crucial in the startup and normal operating functions of the system.
Chapter 7-<number>

## Slide 25
Solenoids are used for general-purpose applications, such as those in airplanes.
Notes: In addition to commercial and industrial use, solenoids are used for general-purpose applications. Typical general-purpose applications include products such as printing calculators, cameras, and airplanes. See Figure 7-17.
Chapter 7-<number>

## Slide 26
Pneumatic robots can be used to replicate human movement with the added advantage of being able to lift objects of almost any size and weight repeatedly.
Notes: Industrial robots are used in all kinds of applications from welding, painting, sorting, and assembling extremely small to extremely large parts. They can replicate human movement with the added advantage of being able to lift objects of almost any size or weight repeatedly in almost any type of environment. Industrial robots use fluid power (hydraulic and/or pneumatic) cylinders (linear motion), actuators (rotary motion), and grippers to provide the required power and movement. The cylinders, actuators, and grippers are controlled by solenoid-operated valves. See Figure 7-18.
Chapter 7-<number>

## Slide 27: 7-4 Checkpoint
What type of valve is used to direct the flow of fluid throughout a fluid power system?
What is the number of locations within a valve in which a spool is placed to direct fluid through the valve?
What is a flow path through a valve?
What does an electrical control valve use to change the position of a valve spool?
Notes: Chapter 7-<number>

## Slide 28: Objectives Section 7-5 Troubleshooting Solenoids
State how transients are caused and how they can be reduced within an electrical system.
Describe the steps required when using a digital multimeter (DMM) to troubleshoot a solenoid within a system.
Notes: Chapter 7-<number>

## Slide 29
Manufacturer charts are used to help determine the cause of solenoid failure.
Notes: Solenoids usually fail due to electrical problems or mechanical damage. Electrical problems include coil burnout, erratic operation, or an open fuse or circuit breaker. Manufacturer charts are used to help determine the cause of solenoid failure. See Figure 7-19.
Chapter 7-<number>

## Slide 30
The voltage applied to a solenoid should be ±10% of the solenoid rated value.
Notes: The voltage applied to a solenoid should be ±10% of the solenoid rated value. The voltage is measured directly at the valve when the solenoid is energized. A DMM set to measure AC voltage is used for AC solenoids. A DMM set to measure DC voltage is used for DC solenoids. The range setting must be greater than the applied voltage. See Figure 7-20.
Chapter 7-<number>

## Slide 31
A DMM set to measure voltage and resistance is required when troubleshooting a solenoid.
Notes: A DMM set to measure voltage and resistance is required when troubleshooting a solenoid. See Figure 7-21. To troubleshoot a solenoid, the following procedure is applied:
1. Turn off electrical power to solenoid or circuit.
2. Measure the voltage at the solenoid to ensure the power is OFF.
3. Remove the solenoid cover and visually inspect the solenoid. Look for a burnt coil, broken parts, or other problems. Replace the coil when burnt. Replace the broken parts when available. Replace the valve, contactor, starter, or solenoid-operated device when the parts are not available. Note: Determine the fault before installing a new coil when a solenoid has failed due to a burnt or shorted coil. Coils will continue to burn out if the fault is not corrected. Always observe solenoid operation after a solenoid is replaced.
4. Disconnect the solenoid wires from the electrical circuit when no obvious problem is observed.
…See complete procedural list on pages 185–186.
Chapter 7-<number>

## Slide 32: 7-5 Checkpoint
What is the acceptable voltage range (high and low) that should be applied to a solenoid?
What device is used to reduce transients produced by solenoids?
What is the acceptable resistance range (high and low) that should be measured when testing a solenoid?
Notes: Chapter 7-<number>