## Slide 1: Management and Operation of the Electrical Grid
Load Management is the process of balancing the supply of electricity on the network with the electrical load by adjusting or controlling the load rather than the power station.
  This can be achieved by direct intervention of the utility in real time, by the use of frequency sensitive relays triggering circuit breakers (ripple control), by time clocks, or by using special tariffs to influence consumer behavior.
  Load management allows utilities to reduce demand for electricity during peak usage times, which can, in turn, reduce costs by eliminating the need for peaking power plants.
  Load management can also help reduce harmful emission, since peaking plants or backup generators are often dirtier and less efficient than base load power plants

## Slide 2: Management and Operation of the Electrical Grid
Role of Utility in Grid Management and Operation
  Responsible for the safe, reliable, and efficient electric transmission system including generation of electricity and natural gas
  Purchase reliable power from a mix of convention and renewable generating sources
  Manage substations and switching points in the electric system, connecting transmission system s to distribution
  Responsible for the individual connections from the transmission lines to customers
The Role California ISO (CAISO) in Grid Management and Operation
  As the impartial grid operator; it is like the air traffic controller for the state’s electricity flow:
    Operates the high voltage grid for most of the state
    Ensures power can flow as intended without congestion or overload
    Keeps supply in balance with demand on a second by second basis
    Coordinates the planning process for proposed grid expansions

## Slide 3: B. Load factor and billing data analysis for Demand Response and Load Shifting

## Slide 4: Parameters for Evaluating Load Shapes
Near-Base Load (kW): 2.5th percentile of daily load.
Near-Peak Load (kW): 97.5th percentile of daily load.
High-Load Duration (Hours): Duration for which load is closer to near-peak load than to near-base load.
Rise Time (Hours): Duration for load to go from near-base load to the start of the high-load period.
Fall Time (Hours): Duration for the load to go from the end of the high-load period to the near-base load.
Notes: <number>

## Slide 5: Visual Observations
Notes: <number>

## Slide 6: Load Statistical Summary (LSS)
LSS a plot of average, minimum and maximum points for a given range of dates.
- Refined to display Near-base load and near-high load (2.5 and 97.5 percentile values) (Price 2010)
Notes: <number>

## Slide 7: Load Variability
Variability of each interval data within a given period is calculated using variance.
If the loads are highly variable (V>15%), the programs that settle using a baseline may not be appropriate for the customer.
Notes: <number>

## Slide 8: Weather Sensitivity
Weather Normalized Demand
Rank Order Correlation is used to determine weather sensitivity
Notes: <number>

## Slide 9: Weather Sensitivity
Rank Order Correlation (ROC) is used to calculate weather sensitivity of buildings
Weather normalization is used anytime we need to compare building performance of weather sensitive buildings.
Less DR opportunity in mild weather and long DR duration
Notes: For ROC:
  Rank all the load and temperature values from highest to lowest for the same hour. For the values that are the same, take the average of the ranks.
  Replace the actual values with the ranks.
  Calculate the correlation of ranks for each hour.
The formula for the Spearman Correlation Coefficient is :
Where 6 is a constant (it is always used in the formula),
D refers to the difference between ranks on the two variables,
and N is the number of days.
<number>

## Slide 10: DR Process
Analyze load shapes
Analyze operations,
systems, and end uses
Assess DR Option
Implement Strategies
Evaluate Effectiveness
1
2
3
4
5
Historical data used for various purposes:
  Visual analysis
  Develop Load Statistical Summary
  Evaluate Load Variability and Weather Sensitivity
  End-use contribution to peak load.
Collect information on end uses, systems, controls and operations
What kind of DR program works for the facility? Mapping load shapes onto rates and programs
Semi- or fully-automated
Calculate shed - is it acceptable? Variable?
Notes: <number>

## Slide 11: Understanding Building Operations
Collect information on building systems, end uses and operations.
Architectural, mechanical and electrical drawings?
Is there any sub-metering? Trend logs?
Any plans for energy efficiency or change in building operations?
Notes: <number>

## Slide 12: DR Strategies
decrease
Notes: LBNL – study results
<number>

## Slide 13: Global Temperature Adjustment
Notes: <number>